DELHI AVIATION FUEL FACILITY PRIVATE LIMITED

(Joint Venture of IOCL, BPCL & DIAL)

Reg. Office: Aviation Fuelling Station, Shahbad Mohammad Pur,

IGI Airport, New Delhi - 110 061, INDIA

BIDDING DOCUMENT FOR PROVIDING PROJECT

MANAGEMENT CONSULTANCY SERVICES FOR

MODERNIZATION OF THE FUEL FARM- IGI AIRPORT AT SHABAD MOHAMMADPUR, NEW DELHI

OPEN COMPETITIVE BIDDING THROUGH TENDERING

TENDER NUMBER: PT/DAFFPL/01/2013-14

CONTENTS

| Sl. No. | Description | Page No. |
| --- | --- | --- |
| 1 | Notice Inviting Tender (NIT) | 03 |
| 2 | Instructions to Bidders | 10 |
| 3 | Project Proposal | 14 |
| 4 | Project Implementation Strategy | 17 |
| 5 | PMC’S Scope of Work | 20 |
| 6 | Obligations of Owner | 27 |
| 7 | General Terms and Conditions | 28 |
| 8 | Special Terms and Conditions | 51 |
| 9 | Price Bid Format | 54 |
| 10 | Payment Schedule | 56 |
| 11 | Annexures |  |
| A | Format for exceptions & deviations | 57 |
| B | Pro forma of Bank Guarantee for Earnest Money Deposit | 58 |
| C | Pro forma of Composite Bank Guarantee for Security Deposit & Performance | 60 |
| D | Letter of Undertaking | 62 |

NOTICE INVITING TENDER (NIT)

A.	Delhi Aviation Fuel Facility Private Limited (‘DAFFPL’) invites applications from Interested Parties (defined below) to submit their respective ‘bid’ (‘Bid’) for PROJECT MANAGEMENT CONSULTANCY (PMC) SERVICES FOR MODERNIZATION OF THE FUEL FARM & OTHER WORKS AT SHABAD MOHAMMADPUR, NEW DELHI, REPUBLIC OF INDIA (‘Project’), on the terms and conditions contained in this TENDER.

The Bid shall be unconditional, firm and valid for a period of 180 (One hundred and eighty) days from the due date of opening. Any Bid having validity lower than that specified above shall be rejected by DAFFPL as being non responsive. However, DAFFPL may, at any time, request the Interested Parties to extend the Bid beyond the period of 180 (One hundred and eighty) days from the due date of opening by written notice to the Interested Parties.

The Interested Party(ies) are advised to visit and inspect DAFFPL’s fuel farm facility located at Shabad Mohammadpur, New Delhi, Republic of India (‘Site’) and its surroundings, and obtain for itself at its own responsibility and cost, all information that may be necessary for preparing the Bid and entering into an agreement incorporating the General Terms and Conditions and Special Terms and Conditions, in respect of the Project (‘Agreement’). The inspection of the Site shall be carried out as per the timeline identified in this TENDER, subject to the security and other clearances, as may be applicable.

Interested Party(ies) may obtain further information from:

- Tender Officer:

Chief Executive Officer,

Delhi Aviation Fuel Facility (Private) Limited

Room no 10, Wing “A” , First Floor,

Terminal 3 Project Office, New Uddan Bhawan,

IGI Airport, New Delhi – 110 037, India

Tel.	+ 91 11 46084200,

Email: rrrao@daffpl.in

The Interested Parties are advised to adhere to the following schedule for the purpose of this TENDER.

Bids are invited under single stage two envelope system from Interested Parties meeting the ‘Bidder’s Qualification Criteria’ as stated in the detailed Bid Document .

B.	Salient Features of Bidding Document

| Type of Enquiry | : | Competitive bidding/Global |
| --- | --- | --- |
| Bid Document | : | Tender no: PT/DAFFPL/01/2013-14 dt 30.08.13 |
| Tender fee ( Non refundable) | : | INR 2500/- (Indian Rupees two thousand five hundred only) for Indian bidders & US $ 50 (United States Dollars fifty only) for foreign bidders |
| Earnest Money Deposit |  | INR 1,50,000/- (Indian Rupees one lac fifty thousand only) for Indian bidders & US $ 3,000 (United States Dollars three thousand only) for foreign bidders |
| Bid Document available date on DAFFPL website |  | 30.08.13 |
| Bid submission date & Time up to | : | 14:00 Hrs on 27.09.13 |
| Date & time of opening of unpriced bids at DAFFPL Office |  | 15: 00 Hrs on 27.09.13 |
| Price bid opening |  | 10:00 Hrs on 04.10.13 |
| Bid Qualification Criteria |  | As per clause no. C of NIT |
| Clarifications should be Obtained within |  | 12 days from the date of issue of the Tender document |
| Response to Clarifications |  | Shall be sent to all parties irrespective of who have asked Within 6-7 days from the date of query/ies. |
| Bid is to be submitted to the corporate office of DAFFPL on or before the due date. Late offers received will be rejected. |  |  |

C.	Bid Qualification Criteria

C.1	Technical:

- Bidder shall itself possess   at least Seven years experience  in  Project Management Consultancy Services including design & detailed engineering for Pipeline, SCADA, Instrumentation & CP systems involving  tank gauging system, flow meters, pressure transmitters, fire and smoke alarm system, flow elements, control valves, relieving and depressurizing devices sizing calculations. Ability to Check and confirm all preliminary process data and sizing, as well as material and type selections of such devices   Preparation of design documents / drawings for Instrument index  PLC / DCS system input / output list PLC / DCS system architecture, Preparation of as-built documentation for instrument data sheets, instrument indices, connection schedules/diagrams, and all control system related documentation, procurement & tendering services, inspection & expediting, testing, site supervision & management,  experience of carrying out Environment Impact assessment, Rapid Risk Analysis & Hazop study of Aviation Fuel Storage facilities, and  Competence to design and check Fire safety systems and facilities.

Familiarity with M.B. Lal Committee recommendations & OISD and knowledge of JIG requirements  will be an advantage.

Qualified Bidders shall have independently executed  or provided Project Management Consultancy  for at least ten projects in Oil & Gas Sector and Aviation Sectors together  with the project work similar to our requirement. The  parties shall indicate the number of jobs executed by them and minimum order value and maximum order value for the projects executed

Bidders shall have a ’quality system’ in force. It shall have multi-disciplinary experience, and should be familiar with relevant standards for Oil & Gas / Aviation sectors like American Petroleum Institute (API), American National Standards Institute (ANSI), American Society of Mechanical Engineers (ASME), Instrumentation Society of America (ISA), British Standards (BS), Deutsche Institute Normen (DIN), Japanese Industrial Standards (JIS), Institute of Electrical & Electronics Engineers (IEEE), and International Standards Organization (ISO)& various applicable Indian standards.

- Bidder shall meet the requirement regarding deployment of key personnel i.e. Project Manager, Resident Construction Manager (RCM), Contracts/ Procurement Manager, Inspection/ Expediting/ QC Manager and Engineering Manager, as mentioned below:

Project Manager - Min. experience of 10 years & Two to Three Project  in Oil & Gas/ Aviation sectors  involving automation  to have handled independently and successfully commissioned.

RCM - Min. experience of 10 years & Minimum one Project in Oil & Gas/ Aviation sectors  handled independently and successfully commissioned.

CV of the above Managers along with other key personnel should be submitted along with the Bid.

C.2	Financial Criteria:

- The average turnover of the Bidder for the last three financial years (2010-2011, 2011- 2012 and 2012-2013, and where the financial year is a calendar year, 2010, 2011, 2012) should be  equal or more than INR 5 Crore (Indian Rupees Five crore only) for Indian bidder and US $ 1 million  (United States Dollars one million only)  for foreign bidder.

- The financial net worth of the Bidder as per latest annual report shall be positive. Bidder shall furnish documentary evidence by way of copies of audited balance sheets including Profit and Loss Accounts along with the Bid to establish Bidder’s conformance to Qualification Criteria.

- Bidder shall not be under liquidation, court receivership or similar proceeding.

C.3	Bidding entity

a.	Only a legal entity may submit a Bid.

b.       Consortiums are not allowed to participate.

C.4	General

- Bidder shall furnish necessary documentary evidence along with the Bid. In absence of such documents, DAFFPL reserves the right to reject the Bid without making any reference to the Bidder or assigning any reason what so ever.

- All the documents related to Bid Qualification Criteria should be duly certified  by a third party agency like  SGS/ GLIS Pvt. Ltd./ IRS/ DNV/ LRIS/ EIL/ TATA Projects/

ULIPL/ RITES Ltd./ ITSIPL/ Intratek for Indian bidders, and for foreign bidders, should be certified true copies duly signed, dated and stamped by an official authorised for this purpose in Indian Embassy / High Commission in Bidder’s country. And if duly audited Balance Sheet, Annual Report etc., are not in English language, then the English translation copy of the same shall be furnished duly certified, stamped and signed by Local Chamber of Commerce along with the original Balance sheet / Annual report and not just merely mentioned.

- Bids must be accompanied with the Bid security / Earnest Money Deposit as mentioned in NIT in the form of Demand Draft or non-revocable Bank Guarantee in favour of M/s Delhi Aviation Fuel Facility Private Limited payable at New Delhi in the prescribed Proforma set forth in Annexure B hereto and issued by any Indian Scheduled Bank which includes Indian Branch of Foreign Bank recognized as schedule bank by RBI. The Bank Guarantee shall be valid for six (6) months from due date of submission of the Bid. Bids not accompanied with requisite Bid Security / EMD shall be considered as non-responsive and such Bids shall be rejected.

- Indian small scale units registered with NSIC and Indian Central Government PSU’s will be issued Bid free of cost. Indian small scale industries registered with NSIC shall furnish valid certificate from NSIC for the same.

- DAFFPL reserves the right to assess Bidder’s capability to execute the work using in-house information and take in account their concurrent commitments and the performance (concurrent or past) during the evaluation of the Bid and may reject the Bid.

- Failure to meet the above Bid Qualification Criteria will render the Bid liable to be rejected. Therefore, the Bidder shall in its own interest furnish complete documentary evidence in the first instance itself, in support of its fulfilling the Bid Qualification Criteria as given above. DAFFPL reserves the right to complete the evaluation based on the details furnished without seeking any additional information. [Note: deleted because point is covered in para e above]

The Bid will be submitted under single stage  in two parts as follows:

PART – I  Technical (UN-PRICED BID along with Bid Qualification criteria)

To be submitted  with the envelop marked Technical Bid & Bid qualification criteria at our Corporate Office complete with all technical details and details pertaining to bid qualification criteria  with all other required documents including Price Schedule WITH PRICE BLANKED OUT, Agreed terms and conditions etc. as enclosed at Annexure to the tender document duly filled in and signed with seal on or before due date and time of Last date of Bid submission to the Corporate Office of DAFFPL.

PART – II (PRICED BID)

To be submitted in an envelop marked Price Bid to our Corporate  Office . Price bid should contain only the prices, without any condition whatsoever. Bids complete in all respects should be submitted along with the technical bid  on or before due date and time of Last date of Bid submission to the Corporate Office of DAFFPL.

Each of  the Technical bid & Price bid should be sealed separately  in a different envelop and both envelops should be marked with the address of the bidder and the envelops should be  placed in a bigger  envelop and sealed. The bids may be revised any number of times before the due date. Only the latest dated bid will be considered

D.	Disclaimer

a.	This request for Bid (‘TENDER’) is being issued for the determination of Interested Parties (hereinafter defined) for the  hiring of  PROJECT MANAGEMENT CONSULTANCY (PMC) SERVICES FOR MODERNIZATION OF THE FUEL FARM & OTHER WORKS AT SHABAD MOHAMMADPUR, NEW DELHI  at its fuel farm facility at New Delhi. This TENDER provides the conditions and timelines and has been prepared by Delhi Aviation Fuel Facility Private Limited to assist interested persons (‘Interested Parties’) to submit a bid in response (‘Bid’) to this TENDER. The information contained in this TENDER is being provided for the limited purposes of enabling the Interested Parties to submit Bid(s) and for no other purpose. In no circumstances shall DAFFPL, or its respective advisors, consultants, contractors, officers, representatives, servants, employees and/or agents incur any liability arising out of or in respect of the issue of this TENDER, or the bid process.

b.	This TENDER is being made available by DAFFPL to the Interested Parties on the terms set out in this TENDER. This TENDER is not being distributed to the public and its possession or use in any manner contrary to any Applicable Law is expressly prohibited. The Interested Party(ies) shall observe any and all applicable legal requirements in submission of its Bid.

c.	This TENDER does not, purport to contain all the information that the Interested Parties and their advisors would desire or require in reaching a decision as to the submission of the Bid. This TENDER is a summary of available information and no reliance shall be placed on any information or statements contained herein, and no representation or warranty, expressed or implied, is or will be made in relation to such information and no liability is or will be accepted by DAFFPL, its respective advisors, consultants, contractors, officers, representatives, employees, servants and/or its agents in relation to the accuracy, adequacy or completeness of such information or statements made, nor shall it be assumed that such information or statements will remain unchanged.

d.	The information does not purport to be comprehensive or to have been independently verified. Nothing in this TENDER shall be construed as legal, financial or tax advice. DAFFPL and its respective consultants and advisors will not be liable for any costs or expenses, howsoever incurred by the Interested Parties in connection with the preparation and/or submission of a Bid. DAFFPL reserves the right to amend this TENDER and any information contained herein at its sole discretion, at any time by written notice to the Interested Parties.

e.	Nothing in this TENDER is, nor shall be relied upon as, a promise or representation as to DAFFPL's ultimate decision in relation to the Project. DAFFPL expects to select an entity for executing the Project in accordance with this TENDER on the basis of the bids submitted by the Interested Parties. Interested Parties shall not, therefore, assume that they will have the opportunity to revise their bids following submission. However, DAFFPL reserves the right to change the basis of or the procedures (including the timetable) relating to the tender process, reject any, or all, of the Interested Parties, not to invite a Interested Party to proceed further, not furnish a Interested Party with additional information or otherwise negotiate with a Interested Party in respect of the Project at any time. DAFFPL does not undertake to accept the lowest or indeed any Bid.

f.	No person other than Mr. R. Ramachandra Rao has been authorized by DAFFPL to give any information or to make any representation, not contained in this TENDER and, if given or made, any such information or representation shall not be relied upon as having been so authorized.

g.	This TENDER is confidential and personal to each Interested Party. The Interested Parties have signed and submitted to DAFFPL, a Letter of Undertaking for Non Disclosure with DAFFPL which, inter alia, prohibits disclosure of any information by the Interested Party to any person or body corporate, except as permitted in terms of such Letter of Undertaking for Non Disclosure and the Interested Party agrees to remain bound by the same. Any failure to comply with the terms of such Letter of Undertaking for Non Disclosure shall entitle DAFFPL to disqualify the relevant Interested Party.

h.	Nothing contained in this TENDER is, or shall be relied upon as, a representation of fact or promise as to the future. Any summaries or descriptions of documents or contractual arrangements contained in any part of this TENDER are only indicative and cannot be and are not intended to be comprehensive, nor any substitute for the underlying documentation (whether existing or to be concluded in the future), and are in all respects qualified in their entirety.

i.	This TENDER outlines DAFFPL’s expectations in relation to the Bid(s) to be submitted by the Interested Parties. DAFFPL, its respective advisers, consultants, contractors, officers, representatives, employees, servants and/or agents do not accept any responsibility for the legality, validity, effectiveness, adequacy or enforceability of any documentation executed, or which may be executed, in relation to the Project. No legal or other obligation shall arise between an Interested Party and DAFFPL unless and until the Agreement has been formally executed between DAFFPL and the selected Interested Party and any conditions precedent to the effectiveness of such Agreement has been fulfilled. DAFFPL shall not be obliged to select and or enter into the Agreement with any Interested Party and reserves its right not to proceed with the bid process and to withdraw from the bid process, or any part thereof, at any time in its sole and absolute discretion.

j.	Each Interested Party must rely on the terms and conditions contained in the Agreement when, and if, finally executed, subject to such limitations and restrictions which may be specified in the Agreement. Any reference to this TENDER in the Agreement or any correspondence between DAFFPL and the Interested Party shall not be construed so as to have the effect of this TENDER forming part of the Agreement.

k.	The Interested Parties are prohibited to effect, undertake, abet or prompt any form of collusion or arrangement by and/ or between any one or more Interested Party(s) (directly or through their advisers or consultants) in an attempt to influence the bid and award process or dispersing any kind of information, which is not factually correct or may adversely affect the competitive bidding process. Giving or offering of any gift, bribe or inducement to any officer/ employee of DAFFPL or to any other person in a position to influence the decision of DAFFPL for showing any favour in relation to this TENDER or any other contract, shall render the Interested Party to such liability/ penalty as DAFFPL may deem proper, including but not limited to rejection of the Bid of the Interested Party.

l.	This TENDER is subject to the Laws of the Republic of India. The courts at Delhi shall have exclusive jurisdiction in relation to any disputes arising from this TENDER or in any manner touching this TENDER.

m.	Each Interested Party's acceptance of delivery of this TENDER constitutes its agreement to, and acceptance of, the terms set forth in this Disclaimer and as set forth in the said Letter of Undertaking for Non Disclosure executed and submitted by the Interested Parties to DAFFPL. By acceptance of this TENDER, the recipient agrees that this TENDER, Letter of Undertaking for Non Disclosure and any information herewith supersedes document(s) or earlier information, if any, in relation to the subject matter hereof.

2.0.	INSTRUCTION TO BIDDERS

- General Instructions

Tender documents shall remain the property of DAFFPL and if obtained by one intending bidder, shall not be utilised by another without the written consent of DAFFPL.

Bidder for the Project shall study the Bid Document carefully and understand the conditions/drawings etc. before quoting. If there are any doubts, it shall obtain clarification from DAFFPL. Bidders’ non-understanding of the  Bid Document and or ignorance shall not be entertained nor shall be treated as basis for legal argument prior to award or at a later date of award.

Bidder may visit DAFFPL’s Fuel Farm at Shahbad Mohammadpur with prior appointment from DAFFPL. The cost of visiting the site shall be at Bidder’s own expenses.

B.	Completeness of Tender

Bidder is responsible for identifying and checking against the contents / documents/ drawings list and specifications index that it has received as part of the Bid Document . Any omissions therein or any omission or shortcoming in the scope of the Project should immediately be made known to DAFFPL.

C.	Discrepancies / Ambiguities

Should Bidder find discrepancies or if the intent and meaning of any of the Bid Document appear unclear or ambiguous, Bidder should refer the matter to DAFFPL for clarification.

Once submitted, under no circumstances, offers shall be withdrawn or modified. Negligence on the part of the bidder in preparing its Bid confers no right for withdrawal or modification of the Bid after the same has been submitted to DAFFPL.

D.	Bid Clarifications & Addenda

D.1	Addressee:

All questions and requests for clarifications or interpretations related to NIT documents shall be addressed in writing to:

Chief Executive Officer,

Delhi Aviation Fuel Facility (Private) Limited

Room no 10, Wing “A” , First Floor,

Terminal 3 Project Office, New Uddan Bhawan,

IGI Airport, New Delhi – 110 037, India

Tel.	+ 91 11 46084200,

Email: rrrao@daffpl.in

D.2	Time Limit for tender:

Bid against this Bid Document must be submitted on or before due date of receipt of the Bid. No extension shall be granted after the due date. .  ”DAFFPL may at its sole discretion extend the timeline for submission of bids”

D.3	Clarification Requests by Bidders

Bidders may seek clarification at any time but within 12 days from the date of issue of the TENDER. Replies to queries raised shall be emailed to all bidders within 6-7  days  irrespective of who had sought clarification for information / necessary action.

D.4	Addenda

Addenda to the NIT may be issued at any time prior to the closing date fixed for receiving Bids, to vary either the Bid period or any part of the NIT documents.

D.5	Integral Part of NIT

All addenda are to be considered as an integral part of the NIT documents. They will be sent in identical form to each Bidder who shall acknowledge such addenda by signing and returning the form of acknowledgement that will accompany the addenda.

D.6	Bidder to Confirm

Bidder is required to take account in its Bid of all addenda received during the Bid period and confirm the same in its Bid.

D.7	Conditions of Bid

- Language

The Bid and all supporting documentation shall be in the English language.

- Incomplete / Late Bids

Incomplete Bids may not be considered and late Bids shall be liable to be rejected.

- On award of the Tender, the selected bidder  will be required to submit the Composite Bank Guarantees (security cum performance) for an amount equal to 10% of the total contract value valid for the entire period till Six  months from the date of  Project close out . Besides above no separate performance guarantee shall need to be submitted.

- Canvassing in connection with the TENDER is strictly prohibited and the Bid submitted by the bidder resorting to canvassing shall be liable for rejection.

- DAFFPL reserves the right to reject any or all offers in total or part without assigning any reason whatsoever.

D.8	Submission of Bids

- Bid shall be submitted to The CEO of DAFFPL/ deposited in the tender box kept  at the corporate office of DAFFPL.

- List of deviations, if any. Bidders shall note that they are permitted to propose technical alternatives or other alternatives bids with their Unpriced Bid in addition to or in lieu of the requirements specified in the Bid, provided they can document that the proposed alternative bids are to the benefit of DAFFPL, that they fulfill the principal objectives of the Agreement, and they meet the basic performance and technical criteria specified in the Bid Document.

- Composite Bank Guarantee for Security Deposit & Performance shall be submitted to DAFFPL sooner after the award of job.

- Profile of Bidders/credentials.

- Details of manpower deployment for office and Site. The sealed bid fee & EMD/ Bid Security should be addressed and delivered in person at 1st Floor of M/s DAFFPL’s corporate office Bids received after the due date and time shall be liable for rejection. Any deviation from TENDER shall be separately listed and sent along with unpriced bid.

D.9	Profile of Bidder

The bidder/ consultant shall furnish the following data/details along with its technical bid:

- List of Clients and experience in execution of Modernization projects, particularly in Oil & Gas / Aviation sector.

- Present and anticipated future commitment of the bidder,  list of assignments / projects presently being handled and names of the clients, schedule contract value of each assignment/project.

- Concurrent commitments especially on Aviation sector projects, names, clients, value and schedule of completion for the Project.

- Details of similar works executed in the last two years along with work order copies and completion certificates.

- Manpower availability in the following format with detailed Organogram:

Manpower Manpower available committed

Technical ------ -------

Non-technical ------ -------l

Detailed organogram (office / site) for the Project with CVs of key persons.

Company profile including annual reports for the last 3 years.

Assignments of dedicated task force giving break up of discipline wise strength proposed for this Project with experience and technical qualification of the key personnel. Bidder shall be required to make presentation on methodology proposed by them to be adopted for completion of Project in line with requirements as laid down in at the time of technical discussion. Methodology of approach particularly conceptual design, estimation and scheduling. Philosophy for the quality assurance & safety at construction site during execution of the Project.

Details of data bank / data base, design support etc. to be sourced by the consultant for respective design of facilities either from internally or externally needs to be clarified.

Latest assessment order by Income-tax authorities.

Schedule of completion of major activities in the form of bar chart.

List of Exceptions / Deviations, if any, shall be as per Annexure-A.

This list given above is not exhaustive. The bidder to include the documents required to be submitted / mentioned anywhere in this TENDER.

D.10	Further Instructions to Bidders for Tendering

a.	Interested parties may download the tender from DAFFPL’s tendering website www.daffpl.in and participate in the TENDER as per the instructions given herein, on or before the due date and time of the submission of the Bid.

b.	Corrigendum/ amendment, if any, shall be notified on the site www.daffpl.in In case any corrigendum/amendment is issued after the submission of the Bid, then such tenderers who have submitted their Bid, shall be intimated about the corrigendum/amendment by email. It shall be assumed that the information contained therein has been taken into account by the tenderer. They have the choice of making changes in their Bid before the due date and time.

c.	No correction, erasure or overwriting is permissible in the priced Bid. The Bidder shall complete the price Bid Form, both in figures as well as in words, in such a manner that no interpolation/ insertion is possible. Should there be a difference between the prices in figures and words, the amount stated in words shall prevail and shall be deemed to be the correct amount.

d.	Accept the contents of the following as a token of your acceptance of the tender conditions:

- Covering letter depicts the purpose of the tender, quantity, tender, type of bids, due date and sections therein.

- Accept the technical specifications / drawings/ scope of inspection (or) fill in the technical specification form as applicable

- Accept the Special Terms and Conditions.

- Accept the General Terms and Conditions

- Make a declaration signed by a director of the Bidder in relation to “Relationship with DAFFPL Directors”, disclosing if the the Bidder or any of its affiliates or its shareholders or shareholders of its affiliates, or its directors have any pecuniary dealings with DAFFPL Directors in the past 12 (twelve) months.

e.	Tenderers are advised in their own interest to ensure that their Bids are submitted well before the closing date and time of bid. If the tenderer intends to change/revise the Bid already submitted, he may do so any number of times till the due date and time of submission deadline.

f.	It shall be understood that every endeavour has been made to avoid error which can materially affect the basis of TENDER and the successful Bidder shall take upon itself and provide for risk of any error which may subsequently be discovered and shall make no subsequent claim on this account. (This should be part of covering letter)

For tender related queries: M/s DAFFPL at contact no. 011-46084200/Mobile: 08826120066

3.0.	PROJECT PROPOSAL

A.	Brief Scope of Work. The brief description of the Project is as under:

A.1	Preamble

Delhi Aviation Fuel Facility Pvt Ltd. (DAFFPL) is a joint venture between Indian Oil Corporation Limited (IOCL), Bharat Petroleum Corporation Limited (BPCL) & Delhi International Airport Private Limited (DIAL). M/s. Indian Oils SkyTanking Limited (IOSL)  is responsible for running day to day operations of receiving the Jet Fuel  and refueling the Air Craft.  It is the responsibility of DAFFPL to provide state of the art facilities to IOSL for facilitating day to day operations effectively so that the Jet Fuel is received, stored and delivered safely. DAFFPL also has to envisage the future requirements and make provisions. The existing system has aged considerably and in view of this it is contemplated to revamp the system incorporating latest technology and safety measures.

A.2	The details of existing facilities are as follows:

Storage Tanks:  4 numbers of 6000 KL and 2 numbers of 9000 KL (Total 42000 KL) Product  is received from IOCL and BPCL from Bijwasan Terminal through  Pipe lines with a flow rate of 200 KL per Hour.

8 bay TT decantation facilities with 2 numbers of 75m3 /Hr - 75 KW pumps.

Delivery side 2x75 KW Jockey Pumps & 8  numbers of  3600 LPM  pumps 160 KW + 2x 4000 LPM -220 KW  pumps.

This station takes care of fuel supply currently for Terminal 2 Cargo & Terminal 3 complete.

Power supply is from  two sources -- 11KV and 33 KV  Coming from two different substations.

Fire fighting facilities covering the tank farm operational area office building etc., are provided already which need to be studied for revamping/redesign.

The P & ID line diagram of the existing system available in the office of the undersigned may be studied with prior appointment.

As the installation is about 25 (twenty five) years old, it is proposed to modernize the installation keeping the following requirements in view

- Currently the pumps are being operated manually monitoring the pressure gauge located in the control room. The line pressure is to be maintained at 12Kg/Sq. Cm. There is no pressure transmitter installed on the delivery line. It is imperative to provide a pressure transducer for monitoring the start of the pumps.

- The tanks have been provided with butterfly type motorized valves on both receipt and delivery line. It is planned to replace these with motorized ball valves /Double Block & Bleed Plug Valves.

- At present, Rosemount tank gauging system is provided on the tanks for providing gauging indication tank wise. We need to have temperature probe, and average density probe for computing the total quantity of the fuel being delivered and received both at ambient temperature and at 15 Deg C.

- It is also imperative to provide for High, High-High alarms and similarly Low, Low-Low alarms with a logic for closing the motorized valves on either alarm.

- It is proposed to change the flow meters installed in the filtration system with state of art meters to accurately compute the total quantity of Jet Fuel passing through each filter and the rate at which the Jet Fuel is passing. This data to be utilized for auto operation of pumps.

- To provide facility in the tank to draw sample from top, middle and the bottom without going to the top of the tank. This is to be achieved by putting flexible SS pipes along the length of the floating suction.

- To design and commission a SCADA system which should take care of the present and future needs apart from being redundant.

- To provide for integration of all the above from 1 to 7 to SCADA system.

- Apart from the above, the outputs from the following also to be integrated to SCADA

- The Diesel Generator system operations & the  Variable Frequency Drives (VFD )

- Cathodic Protection for both the T3 and T2

- E S B ( Emergency Switch Off Button  operations ) on T3 and T2

- The existing illumination is to be studied and augmented by providing additional Flame Proof flood lighting.  The switching on and off  of power to flood lights to  be automatic based on timer system. Video cameras with Pan & Zoom functions to be installed for monitoring the   complete area of the fuel farm.

- To provide additional fire alarm points inside the terminal.

- Provide for smoke detection and water sprinkler, fire alarm system inside the office building.

- To add public address system in the fuel farm.

A.3	  To make modifications as follows:

Currently Jet Fuel is received from both IOCL and BPCL by pipelines from Bijwasan               Terminal.

- The two pipe lines provided on the receipt side can cater to either two pipe line transfers or one pipe line transfer and one    TT decantation simultaneously as    one  of the pipe lines is connected to the TT decantation line. We need to separate and provide a separate TT decantation line which would enable to operate the two pipe line transfers and one TT decantation simultaneously.

- Currently there are no flow indicators on any of the receipt lines. It is proposed to get a flow meter installed and the results integrated with SCADA.

A.4	Currently the location has 2x200 KL tanks for taking the drained product into them after quality control

- We need to have a fast flusher sampling system (closed circuit quality control system) to be installed at each tank with 1.5 HP flame proof motor to push back the product into the tank. (A copy of sampling system is enclosed).

- After this arrangement it would be possible to use one 200 KL tank for offloaded product from Aircrafts to be kept in the tank.

- One 70 KL tank is to be fabricated   to enable the operator for storing the downgraded product.

- After fast flusher is installed we would like to redo the flooring of the tank farm  by concreting  and to construct the Bund wall as per OISD norms.

- The earthing points are inside the tank farm area and are to be brought out and commissioned.

- A new oil water separator of latest technology to be installed within the fuel farm.

- After completion of providing the facilities as planned to provide for HAZOP study pertaining to this location only.

A.5	Electrical and the Control Room

- To study the existing MCC and the newly provided Variable Frequency drives and to suggest modifications and modernization in order to have safe operations both on 33 KV line and 11KV line individually or on  combination .

- To suggest safety system to be added for safe operations.

- To replace the existing control panel and to provide a new modern panel where the shift controller can control the complete Fuel Farm operations sitting at one place.

- The control panel to have four to five monitors so that the receipt and delivery operations can be monitored along with other functions mentioned under SCADA to be integrated.

- To provide a proper lightening arrester and to earth the same in a suitable and safe place.

A.6	To address the safety requirements thoroughly by studying facilities and filling gaps with respect to safety.

A.7	To study the existing dyke containment, suggest suitable modifications as per the latest OISD norms, chalk out a plan for providing impermeable HDPE membrane in the dyke area.

A.8	To design New ATF storage tanks based on the projected requirement & suggest location for the same in the fuel farm area.

A.9	As mentioned above, all the outputs should be integrated to SCADA and various levels of SCADA monitors should be provided.

The above may not be exhaustive requirement. The proposed consultant shall make a comprehensive study of the installation and suggest further modernization and prepare the Road Map for the project.

To prepare all the drawings in CAD subsequent to the completion of Modernization and other works.

The prospective PMC on whom the order will be placed will execute the project in EPC mode as per the terms and conditions described elsewhere in this document

4.0.	PROJECT IMPLEMENTATION STRATEGY

A.	It may be noted that the specified Modernization & other works have to be carried out at the fuel farm which is a live station. It will not be possible to shut down the station.

a. 	The scope of services is as per Sl. No. 5.0 of the index of the tender document but not limited to the following:

i. 	The scope of Project Management Consultant (PMC) is to execute the project right from Design to Commissioning & project close out on total and single point responsibility basis.

ii. 	The PMC Project Manager will be the “Engineer-In charge” for the said Project.

iii. 	The scope of work of the PMC is broadly defined under the following heads but not limited to the main scope of work envisaged is Design Engg., Tendering/Procurement, Execution Supervision (Office/ Site), and Monitoring & Commissioning of the Modernization of the Fuel Farm as described above.

b. 	Design & Detail Engineering, including other technical document related to the job.

c. 	Planning & Scheduling

d. 	Preparation of detailed specifications for tendering & providing vendor list. However, Tendering & Ordering including Purchase of all equipment and materials, Customs Clearance and Transportation of materials/ equipments to site etc. will be the responsibility of DAFFPL

e. 	Coordinating in Inspection/ Expediting of equipment/Materials being manufactured by vendors including contractors supplied items.

f. 	Arrangement and Management of Construction Stores

g. 	Construction Management & Supervision

h. 	Project Commissioning.

i. 	Project Cost Control, Management & Monitoring.

j. 	Carrying out Environment Impact assessment, Rapid Risk Analysis & Hazop study of the facilities.

k. 	Health & Safety Management

l. 	Project closeout

B.	The time of completion for the preparation of a detailed consultancy report and a road map for Modernization of the Fuel Farm & initiate procurement process shall be 2  months from the Award date of the TENDER

DAFFPL advises the consultant three major milestones for working out the Completion schedule of 12 months.

First Target Milestone – 2 months from the Award date - Preparation of a detailed consultancy report and a road map for Modernization of the Fuel Farm, initiate procurement process.

Second Target Milestone - 8 months from the Award:  Completion of all the procurement required for   Modernization  & other activities

Third Target Milestone – 11th to 12th months from award date - Completion of modernization works, stabilization of SCADA and closure of all contracts & post commissioning stabilization.

C.	Contract Period

Contractual scheduled time for the PMC contract shall be 12 months.

The PMC would prepare detailed schedule in consultation with DAFFPL at the beginning / during kick-off. All efforts should be made to meet all the intermediate schedule and milestones. PMC is required to plan and deploy manpower and resources accordingly. PMC is required to work simultaneously in various packages and works and make all out efforts to complete the Project on or before scheduled date.

D.	General

D.1		Bid document is non-transferable. Bids received from bidders in whose name Bid Document Fee has been submitted shall only be considered. Bidder must submit the Bid Document Fee in their name. Bid Document Fee will be submitted by Bidders as per Instructions to Bidders.

D.2	Payment of Bid Document Fee shall be Crossed Bank Draft from an Indian Nationalized / Scheduled Bank, in favour of DAFFPL, payable at New Delhi and the same shall be submitted in physical form along with Bid Security/EMD. Bank Draft shall be valid for 3 months. The bid of any bidder shall be considered only if the bid is accompanied by the prescribed bid document fee in the form of demand draft along with the Bid Security.

D.3	The firms registered with NSIC (under its single point registration scheme) will be exempted from the bid document fee provided they are registered for the items they intend to quote. The Government Department / PSUs will also be exempted from the payment of bid document fee. However, Industries registered with NSIC shall provide necessary documentary evidence, whereas PSUs shall submit declaration to this effect that they are a PSU and are eligible for getting bid documents free of cost.

D.4	Public Sector Undertakings and firm registered with NSIC are exempted from  furnishing Bid Security, provided the firms are registered for the items, they intend to quote and subject to their enclosing with their bid a copy of latest and current registration certificate.

D.5	Small Scale Industries registered with NSIC under its single point registration scheme shall be exempted from submission of bid security/ EMD subject to their enclosing with their bid a copy of latest and current registration certificate.

D.6	DAFFPL will not be responsible for cost incurred in preparation and delivery of bids.

D.7	The following documents must be submitted in Original

a. 	Demand Draft towards Bid Document Fee

b. 	Demand Draft/BG towards EMD/ Bid Security

c. 	Power of Attorney

D.7	The complete Bid Document is available on DAFFPL Tendering website www.daffpl.in

D.8	DAFFPL reserves the right to reject any or all the bids received at its discretion without assigning any reason whatsoever.

D.9	This Notice Inviting Tender (NIT) is an integral and inseparable part of the enclosed Bid Document.

Yours faithfully,

For DAFFPL

R.R.Rao

Chief Executive Officer

5.0.	PROJECT MANAGEMENT CONSULTANT’S SCOPE OF WORK / SERVICES

A.	The CONSULTANT (i.e., selected Bidder with whom the Agreement is executed) will act as an extension of OWNER (i.e., DAFFPL), always keeping in view OWNER’s interests and advising / guiding the OWNER on all important matters, to ensure the project is completed within cost, time and quality targets.

The CONSULTANT shall perform services comprising Project Management, Process Engineering, Detailed Engineering, Procurement services, Construction Management, Pre-commissioning, Commissioning and Post commissioning stabilization, etc. for the Project.

The scope of services shall be for a period of  12 months  from the date of work award. All necessary manpower / infrastructure facilities shall be maintained by CONSULTANT for site / office for executing of the Project for achieving project completion.

B.	The salient features of scope of CONSULTANT’s work for each facet of Project activities are described under.

B.1	CONSULTANT shall have the primary responsibility of completing and commissioning the Project within the agreed time schedule, cost estimates and ensuring quality of procurement items and workmanship in line with sound established engineering practices, standards and codes.

B.2	CONSULTANT’s scope of work for the Project shall cover services pertaining to basic design, detailed engineering, vendor identification, procurement activities including   inspection and expediting, short listing of contractors, tendering, construction, supervision, stores management commissioning supervision, closing of contracts and overall project management.

B.3	CONSULTANT would undertake basic & detailed engineering, procurement of materials / equipment , prepare detail specification for procurement & contract packages, prepare tender document for procurement & works contract, floating of tenders, techno-commercial discussions/ evaluation, recommendation, opening price bids and preparing final recommendation for award, preparation of draft LOI, construction supervision, quality assurance, ensuring safety at Site as per OWNER laid down guidelines, pre-commissioning and commissioning and post  commissioning stabilization, stores management incl. Receipts / storage /issues & materials reconciliation, concluding contracts etc.

B.4	The documents submitted by the CONSULTANT shall be atleast 98% accurate with respect to the design parameters, process parameters, and other statutory / Govt. provisions.

B.5	In principle approvals from statutory authorities shall be arranged by CONSULTANT.

C.	Detailed Engineering

This shall include preparation of specifications, drawings and documents required for     issue of tenders/ tenders for procurement and construction services, not limited to but as broadly detailed below:

Provision of modernization to the fuel farm equipment in general & specifically the following:

- Pressure transmitter, High, High- High, Low, Low- Low Alarms Tank gauging, Flow meters provision

- Replacement of Motorized valves.

- Review / update of the existing dyke and sampling system

- Prepare typical construction drawings

- Review / update Alignment Drawings and other relevant details.

- Preparation of conceptual designs for Cathodic Protection (CP), telecommunication, Supervisory Control & Data Acquisition (SCADA) turnkey Instrumentation keeping all  the above in view.

- Arrange to prepare detailed "approved for construction "drawings

- Carry out pressure calculation and stress analysis of piping systems.

- Prepare single line diagrams of Electrical systems and finalise load list for power and lighting loads to identify equipment ratings.

- Prepare Material Take Off (MTO), Bill of Material (BOM) for all procurement items.

- Technical specifications for laying of pipeline / erection of equipments etc.

- To review / approve the drawing / documents prepared by vendors / contractors for execution of the works.

- To carry out inspection at Vendor's works for direct procurement items.

- Provide design data / drawings / calculations & all the necessary technical support as required for statutory clearances / NOC's from various Govt. / other agencies.

- Identify estimated power requirement on priority and extend help to OWNER in submitting application to Electricity Board / Statutory authorities.

- Any other activity considered necessary.

D.	Tender / Tender Packages

All tendering shall be done as per  PSU standards  . The number and scope of individual contracts will be finalized by CONSULTANT in consultation with OWNER depending on availability of contractors with multidisciplinary experience and adequate financial standing. Tentatively the following contracts are envisaged.

E.	Tendering / Tendering Services

- Arrange for pre-qualification of construction contractors through press advertisement when adequate number of parties for the respective job are not available in CONSULTANT’s/ OWNER’S approved list, prepare a list of parties and obtaining approval of OWNER for the same.

- Where adequate number of parties are available in-house with CONSULTANT, prepare list for the same for each package to be tendered and obtain approval of OWNER for the same. OWNER may add or delete names as per their in-house record of performance of such contractors. In case, any name is added by OWNER, responsibility for verifying credentials rest entirely with CONSULTANT before issuance of tender.

- Prepare list of supplier / vendor for equipment and material sourcing and obtaining approval from OWNER for the same.

- Finalise General conditions of contract / Special conditions of contract in consultation of the OWNER.

- Prepare draft tender/ tender document, obtain comments from OWNER, incorporation of the comments if considered relevant after discussion, finalise tender/ tender document, seeking OWNER’s approval of the final tender document for issue of tenders/ tender and float them to the parties as approved. Consultant shall prepare both block & detailed estimate of the work packages in line with market rates & local construction material rates before raising of the tender

- Carry out technical and commercial evaluation of bids, prepare recommendation for short-listing of parties and opening their price bids after OWNER’s approval, prepare evaluation of bids, formulate recommendations for negotiation / award for OWNER’s approval. Also follow the various stages of tendering processes in case of tenders. In case negotiation is to be carried out, CONSULTANT shall assist OWNER during price negotiation. Subsequently CONSULTANT shall provide brief justification in case final prices after negotiations are found substantially higher than the detailed estimates. Prepare draft Fax of Intent (FOA), Detailed letter of Acceptance (DLOA), Complete contract documents and agreement.

- Detailed tendering/ tendering processes shall be evolved with selected PMC.

- Any other activity considered necessary for execution of scope as per norms.

F.	Construction Supervision

- Finalise construction related procedures such as quality assurance, safety at construction site, etc.

- Finalise progress report formats. CONSULTANT shall prepare weekly site progress / monthly progress reports. Monthly progress report for the whole project shall be forwarded to OWNER as per agreed time schedule.

- Prepare detailed project execution /construction schedules (bar-chart), manpower / machinery deployment plans and review the same periodically.

- The three major milestones for working out the completion schedule of 12  months shall be as follows:

First Target Milestone – 2 months from the Award date - Preparation of a detailed consultancy report and a road map for Modernization of the Fuel farm, initiate procurement process.

Second Target Milestone - 8 months from the Award:  Completion of all the procurement required for   Modernization  & other activities

Third Target Milestone – 11th to 12th months from award date - Completion of modernization works, stabilization of SCADA and closure of all contracts & post commissioning stabilization.

- Dedicated manpower and resources for supervision to be deployed considering two spreads for execution of the job work may be carried out on 24-hour rotation basis depending upon circumstances and pace of progress to complete the same within the given target of 12 months (Commissioning).

- Review, co-ordinate and supervise closely CONTRACTOR’s work to ensure that the work executed and supplies made are strictly in accordance with the specifications laid down in the Agreement.

- Review progress of work weekly / monthly / quarterly with participation of head office and site representatives from OWNER / Consultant / Contractor , identify bottlenecks and take corrective measures to meet the target.

- CONSULTANT shall arrange to take measurements of works along with contractor’s representative and certify all bills for payment. OWNER’s representative shall also associate during physical measurements and will arrange to make payments thereafter.

- CONSULTANT shall certify material reconciliation statements prepared by the contractors for OWNER supplied materials.

- CONSULTANT shall arrange for preparation of As-built drawings through contractors duly certified by them and submit in 6 copies to OWNER.

- Issue certificate for completion of works and work completion certificates to contractors engaged.

- To provide necessary assistance to OWNER for conducting negotiations with contractors for items, which are expected to undergo large variations.

- Certify / settle final bills for closing of contracts.

- Provide back up support for any audits/queries.

- Adherence of DGCA, MOP & NG, other Govt./ statutory guidelines for big projects.

- Any other activity considered necessary.

- CONSULTANT shall have overall responsibility for management of work sites and coordination among contractors.

G.	Procurement / Procurement Services

G.1	CONSULTANT’s scope shall include, but not limited to, following services for procurement /procurement of direct procurement items incl. All major / long lead / critical items:

a.	Arrange for identification of vendors from CONSULTANT’s approved list. In case, adequate number of vendors for procurement of particular material is not available with CONSULTANT / OWNER, pre-qualification with press advertisement in consultation with the OWNER.

b. 	Prepare agreed vendor list for direct procurement items and formulate purchase procedures for imported and indigenous items in consultation with the OWNER.

c. 	Prepare tender document for procurement/ procurementof direct procurement items (indigenous / imported materials) send the draft document to OWNER for comments if any, incorporate OWNER’s comments after discussions, prepare final document and obtain OWNER’s approval for floating of tender.

d. 	Receipt of bids, carry out Technical & Commercial evaluation, arranging discussion with parties, prepare techno-commercial evaluation of bids & short listing of parties, obtain OWNER’s approval for list of parties short listed, prepare recommendation for opening price bids and obtain approval from OWNER, open price bids, carry out price evaluation and recommendation for negotiation / award, assist OWNER in negotiations if required & prepare draft FOA. Also follow the various steps / stages of procurementprocess in case of e-procurement.

e. 	Prepare detailed purchase order along with complete technical specifications for issue by OWNER.

f. 	Approve manufacturing procedures wherever necessary and identify materials to be used by vendor.

g. 	Approve vendor drawings and design calculations. The consultant should clearly specify in the Project schedule the time period between receipt of bids from vendors / contractors till preparation of technical bid recommendations. However, this period shall not exceed 1 ½ month in general.

h. 	Carry out stage wise inspection; witness Factory acceptance tests at vendor's works (indigenous / imported). Witness and certify performance / acceptance tests as per purchase specifications and issue Inspection Release note. Scope includes carrying out FAT / SAT, issuing completion certificate, SAT’s reports, Trial runs, etc. This also includes visits to foreign vendor premises for this purpose.

i. 	Monitor progress at vendor's works periodically & expedite procurement activity & send monthly report to Owner informing the procurement status / bottlenecks.

j. 	Stores Management (including dump yards) for supply items including receipt, storage, issue of material to contractors, maintaining records and reconciliation of the same. Dump yard management shall be in the scope of the Consultant and shall include activities like receipt, storage, issue and reconciliation at the end of the Project. DAFFPL shall provide land space for storage of Project material at Site DAFFPL shall also provide necessary security arrangement at these places.

k. 	Consultant shall arrange to take measurements of items supplied by vendors in presence of supplier’s & OWNER’s representative and certify supplier's bills for payment. OWNER will arrange to make payments thereafter.

l. 	Consultant to make all efforts so that surplus material generated from the Project does not exceed 2% of material cost.

m. 	Detailed procurement processes shall be evolved with selected PMC.

n. 	Any other activity considered necessary.

H.	Procurement/ items:

Consultant shall include in the scope of works of vendors adequate spares for various items of procurement which shall include the following:

- Commissioning Spares

- Start- up Spares

- Maintenance Spares

Any other activity necessary to ensure right quality of supplied material / equipment shall be undertaken by CONSULTANT.

I.	Pre-Commissioning / Commissioning / Stabilization

- Prepare pre-commissioning and commissioning procedures

- Check and approve contractor’s manpower, equipment and material deployment for pre-commissioning, and commissioning activities.

- Carry out field checks and trial runs necessary to certify readiness for commissioning of individual systems.

- Coordinate & witness System tightness tests, Relay testing & insulation tests for electrical cables & equipment, Tank gauging system, Alarm system, Flow meters etc.,

- Any other activity deemed necessary for pre-commissioning.

- Define successful commissioning in terms of proving of facilities for their rated performance.

- Providing for CCTV, PA System etc., Additional flood lighting, fire alarm systems within office building and the fuel farm etc., and all the works as defined.

- Co-ordinate with vendors for arranging their commissioning Engineers and supervise commissioning.

- Deploy necessary manpower for commissioning of Motorised valves on the pipeline, Construction of dyke wall, Provision of impermeable membrane etc.,  . Scope includes supervising commissioning to the satisfaction of OWNER.

- After successful commissioning of the SCADA, the scope of PMC includes post commissioning stabilization which includes attending to site related problems of equipments / package vendors / system and ensure system stabilizes to the satisfaction of the OWNER.

J.	Documentation

- CONSULTANT shall arrange AS-BUILT drawings & documents in 6 sets from various vendors / contractors along with reproducible CD’s etc.

- Compile Technical Data Sheets & process parameters for all equipments / machinery / systems.

- CONSULTANT shall arrange Operating & maintenance manuals from vendors / contractors in 6 sets.

- Compilation of Inspection release notes / certificates for all the materials

- Compilation of various Reconciliation statements for direct supply items.

- Providing the P & ID drawings post Modernization & incorporation of SCADA & other works.

K.	Training

CONSULTANT shall include Training to OWNER 's project / operating personnel to facilitate supervision of erection/ testing activities & operation / maintenance of the equipments/ systems in the scope of relevant contracts / purchase orders viz. SCADA, and all components  in consultation with OWNER.

L.	Project Management

- Prepare  project scope and project schedule in consultation with OWNER.

- Prepare list and schedule for drawings to be issued for construction.

- Prepare typical formats for documents required for monitoring and progress reporting viz., drawing schedules, MR schedules, procurement status, inspection status and construction status etc.

- Develop co-ordination procedure to establish formal lines of communication between OWNER and CONSULTANT.

- Preparation of Project Status Reports for submission to various agencies.

M.	Cost Estimates

Cost estimate for individual packages shall be prepared by CONSULTANT in two stages. In the first stage estimates shall be prepared on block basis to ascertain Earnest Money value and shall be sent to OWNER for approval along with Bidders qualification criterion/ approval of listed parties as the case may be . In the second stage detailed estimates shall be prepared by the CONSULTANT based on its data bank and as per market conditions. These estimates shall be used for comparison of prices quoted by the vendors. The detailed cost estimates shall be forwarded to OWNER along with price bids and final award recommendations. There should not be major variation between block & detailed estimates.

N.	Statutory Approvals

In principle approvals from statutory authorities shall be arranged by CONSULTANT. The terms and conditions put forth by various authorities shall also be provided to OWNER. Preparation of construction drawings for obtaining necessary approvals from statutory authorities shall be the responsibility of CONSULTANT.  CONSULTANT shall also render necessary assistance / support to OWNER to obtain licences, approvals, clearances, permit etc. as and when necessary by way of providing technical details/ assistance & discussions/ presentations in the meetings. Maintaining of all statutory books, site records/ reports in line with statutory agencies requirement such as CTE etc.

O.	EIA/ RRA/ HAZOP STUDIES

Consultant shall arrange for  carrying out EIA/ RRA/ Hazop studies for the project by floating tenders  & including presentations to the concerned authorities, if necessary. All the necessary assistance to be provided by the consultant for obtaining clearances/ approvals such as Environment Clearance, Pollution Control Board approvals etc.

P.	General

LAND REQUIREMENT FOR THE PROJECT

CONSULTANT shall examine the total land requirement for installation of additional tanks.

6.0.	OBLIGATIONS OF OWNER

A.	OWNER shall be responsible for providing/ arranging the following information, services and assistance at no cost to CONSULTANT:

- OWNER shall provide the approval to the tender packages within 20 (twenty) days of receipt from CONSULTANT. Approval of OWNER on all other documents submitted for OWNER’s approval shall be given within 15 (fifteen) days.

- The CONSULTANT shall arrange for their office space and site office, office furniture & other accessories

- OWNER shall make available basic design data to the CONSULTANT to review and adopt: Product specifications, Copy of terms & conditions of statutory approvals. Arrange marine-cum-storage-cum-erection insurance including transit risk insurance for total works and equipments. To deal with insurance agencies for settlement of claims. Necessary assistance shall be provided by CONSULTANT, without any charges.

- Act as principal employer and deal with all state / Local Govt. regulations, Labour Commissioner, Central Govt., Statutory authorities and Govt. Auditors.

- Carry out selection of spare parts for the plant and procurement of oil, grease, lubes, chemicals, consumable etc. required for commissioning.

- CONSULTANT will give details and brand name of the lube / grease / chemicals / consumables etc. in advance for OWNER to procure the same. Wherever mandatory spares to be ordered with main equipment the same shall be identified by CONSULTANT and consent of OWNER will be obtained. Maintenance spares for 2 (two) years operation will be selected by OWNER.

- Since the system wise commissioning of the project is envisaged progressively between 1 to 2 months after mechanical completion, OWNER will arrange the required inputs, men and operating personal and take over the facilities, system, plant/ unit wise within the period of 1 to 4 months mentioned above.

7.0.	GENERAL TERMS AND CONDITIONS

The following expressions here under and elsewhere in the Tender documents used shall have the following meanings unless otherwise specified.

ARTICLE-1

  - DEFINITIONS

“OWNER” shall mean “DAFFPL” and shall include its successors and assignees, except as otherwise expressly provided or unless the context otherwise requires, in this Contract, the following terms shall have the meanings set forth below:

“Acceptance of the Work” shall mean acceptance by OWNER of the Work.

“Approval/ NOC” means approval in writing by an authorised signatory of OWNER or Consultant (as the case may be) and “approve” or “approved” shall be construed accordingly. Shall also include permissions issued by THE OWNER / any other Govt. / private agencies as required for execution of the project.

“Contract” means this Contract and the Exhibits hereto.

"Contract Price "means the lump sum fixed price payable by OWNER to Consultant in  consideration of performing the Work, in accordance with the terms, conditions and provisions of this Contract".

“Design Information” means any designs, drawings, technical data, reports, surveys or other documents or other written information of any kind supplied by OWNER to Consultant, or to which Consultant is referred by OWNER, whether or not prepared by or on behalf of OWNER.

“NIT ” means the bid documents prepared by OWNER  for the purpose of inviting bids from consultants, for assisting  in design , Engineering, Procurement, Construction and Commissioning of the Project as Project Management Consultant.

“Key Personnel” means individuals who are considered by OWNER to be critical to  the completion of the consultancy Work in accordance with this Contract and notified by OWNER to Consultant as being key personnel.

“Letter of Intent” means the letter issued by OWNER to Consultant appointing the Consultant to commence Work, pending signing of the Contract, in order to facilitate an early start of the project.

“Labour / /consultant/engineer/specialist ” means Consultant’s manpower.

“Materials” means drawings, documents, reports, outputs on floppies etc. to be furnished in connection with the performance of the Work.

“Milestone” means the milestone to be achieved by a specified date or within a specified period.

“Milestone Value” means in respect of any Milestone that part of the Contract Price payable in respect of completion of that Milestone.

“Parties” shall mean OWNER and Consultant, and “Party” shall mean either of the parties.

“Person” means any person, firm, corporation or other legal entity whether incorporated or unincorporated.

“Project Co-ordinator” shall mean Consultant shall appoint, subject to OW NER’s prior written approval, a fully qualified, experienced and competent project Co-ordinator who shall have complete and entire responsibility for executing all work to OWNER’s satisfaction.

“Progress Schedule” shall mean the time schedule of progress of Work.

"Zero date" The Zero date for the project shall be considered as date of receipt of LOI for the purpose of Contract.

“Remuneration” shall mean charges payable to the successful bidder in lieu of services provided under the scope of this Contract.

“Scope of Work” means the all activities to be undertaken by Consultant.

“Tender Documents” shall mean the Tender Documents comprising Notice Inviting Tender, General Conditions of tender, Scope of work, remuneration to bidder and other enclosures of this document along with  amendment, if any

“Work” means the engineering and design services and Project Management Services till commissioning, more fully described in the Scope of Work to be provided in accordance with this Contract, all necessary work and services to be performed by Consultant to satisfy its obligations under this Contract.

“Work Value” means immediately upon notice of termination of this Contract by either Party, the Parties shall consult with one another in order to agree on the percentage of Work completed up to the date of termination. It is understood that resolution of disagreement, if any, in arriving at completed work value will be a matter of arbitration.

  - INTERPRETATION

- All headings of the Clauses in these General Conditions of Tender are intended solely for the purpose of giving a broad indication of the contents of the clause and not as a summary of the contents thereof.

- Unless otherwise specifically stated, a masculine gender shall include the feminine and neutral gender and vice versa and the singular shall include the plural and vice versa.

- The word “SHALL” used in this tender document indicates mandatory requirement. Subject to any express provision to the contrary contained elsewhere in this Contract any period of time fixed by this Contract or determined pursuant to this Contract for doing any act or thing shall be reckoned in accordance with the following provisions:

- the usual non-working days of the week and public holidays in India shall be included in any such period of time;

- “month” shall mean a calendar month;

- where the act or thing is required to be done within a specified period after or from

a specified Date, the period shall begin immediately after that Date;

- where the act or thing is required to be done within or in not more than a specified

period before a specified Date, the period shall end immediately before that Date.

- Wherever in this Contract provision is made for the giving or issue of any notice, consent, approval, certificate, instruction, request, or determination by any Person, unless otherwise specified, such notice, consent, approval, certificate, instruction, request, or determination shall be in writing and the words “notify”, “certify”, “instruct”, “request”, or “determine” shall be construed accordingly.

ARTICLE-2

  - CONSULTANT’S W ORK AND RESPONSIBILITIES

Work: Consultant shall perform the work as scope defined in this tender. Additional responsibilities except as may otherwise be specifically provided in this Contract, Consultant shall be responsible for providing managerial, design and engineering services and labour (Consultant’s manpower) and all materials (documents, drawings, reports, output on floppies, etc.) , stores management and any other items required to perform its Scope of Work.

Special Requirements: Consultant shall comply with the quality assurance requirements, the health, safety and environmental requirements.

Information as to Local Law: Consultant will be responsible for obtaining all information relating to laws, regulations and ordinances, including safety regulations, OISD, and applicable to the performance of Consultant’s obligations hereunder.

Permits and Licenses: Consultant will provide all technical and managerial assistance needed/sought by OWNER to obtain and maintain any registrations, licenses (including import licenses, if any, for the Work), compliances of OISD,DGCA ,PESO and other relevant provisions and permits which are required by any applicable Indian laws or regulations and which are required to be in the name of OWNER or its employees or agents.

ARTICLE-3

  - SCHEDULE OF W ORK

Commencement of Work: Consultant shall commence the work pursuant to award of contract”. The Consultant shall perform its obligations pursuant to this Contract in accordance with Schedule of Work. Time is of the essence and Consultant recognizes the importance to OWNER of the completion of the Work in accordance with the Schedule of Work. The Zero date for the project shall be considered as date of receipt of LOI for the purpose of Contract.

Work Program: Within 7 to 10 days from award of contract, Consultant shall commence work and shall submit to OWNER for approval a detailed program showing how Consultant proposes to perform the Work in accordance with the Schedule of Work. This will be accomplished through a kick off meeting.

Priority of Work: Consultant shall give the Work the due priority and shall not make any allocation of its resources which would have the effect of delaying the timely performance of the Work.

The schedule of 12 months is based on the following assumption:

- All statutory clearances, Land will be made available by OWNER as per project requirement.

- All critical datasheets & P&IDs shall be released within two months after award of contract.

- Delivery of al balance quantity of tagged / bulk items at site are to be ensured at least 2 months prior to mechanical completion.

- All the components required ie  motorized Valves, Tank gauging systempressure transmitter,flow meters etc., will be arranged to be procured by drafting detailed specification and initiating the procurement action well in advance so that the project gets completed within the stipulated time of 12 months.

ARTICLE-4

  - CONSULTANT’S ACCEPTANCE OF THE WORK

EXECUTION OF AGREEMENT

Acceptance of the Work Generally:

The successful tenderer shall execute a formal agreement with the Owner on the owner's format after award of job within reasonable time limits but before raising bills against work done.

Consultant shall acknowledge that it shall enter into Contract for the consideration set forth herein and that Consultant shall carefully examine and satisfy himself in respect of all pertinent matters which may bear upon the performance of the Work, the calculation of the Contract Price and the determination of the Schedule of Work, including, without limitation, the quality and quantity of the Materials required for the performance of the Work, the availability of labour and personnel for such performance, the character and quality of the Work to be performed, the location where the Work is to be performed and any and all other pertinent matters and conditions.

ARTICLE-5

STANDARDS OF PERFORMANCE

In performing the Work, Consultant shall conform in all respects to the standards of performance hereinafter set forth.

  - Professional Performance: Consultant shall perform the Work in a professional manner, using sound good engineering and design principles and management and supervisory procedures, and in accordance with the highest standards of care employed by leading engineering firms. Consultant represents that it has the required skills and capacity to perform the work in the foregoing manner. Management, Design and Engineering.

Management, Design and Engineering Consultant shall perform the work to conform with the requirements of this contract, including without limitation, the Scope of Work.

Documents, Drawings and Manuals: Consultant shall submit to OWNER for comments/review and perusal, within the time periods specified or within agreed periods, such documents, write-ups, designs, drawings, models and manuals as may be specified in the contract.

  - Provision of Services.

General: Except for items required to be provided by OWNER pursuant to this contract, Consultant shall provide all Materials, services of others, supplies and utilities, services required for the design and performance of the work as consultant.

  - Compliance with Codes and Standards.

Consultant agrees that the work and all systems, components and parts of the work shall comply with:

(i) those design criteria, codes and standards which are specified in the contract and

(ii) the requirements of all relevant Indian authorities, including without limitation to :

. Factories Act;

. Indian Petroleum Rules/ India Electricity Rules;

. Tariff Advisory Committee Guidelines;

. Requirement of Chief Controller of Explosives

. Requirements of local bodies and statutory agencies etc.

. OISD standards/ NACE standards for cathodic protection

. Any other requirements

Consultant also agrees that all design criteria, codes and standards included in this Contract are and at all times prior to the Acceptance of the Work will be in compliance with the requirements of such authorities.

Any modification to agreed design criteria will be subject to Consultant providing detailed justification and OWNER’s approval of the same.

  - Conduct of Work:

Manufacturing Procedures: Consultant shall perform, design and develop the Work in accordance with the latest practicable techniques and innovations consistent with the management, engineering and design of the Work and the Schedule of Work. Consultant shall also perform the management, design and development to incorporate, consistent with the Schedule of Work, experience gained in the course of designing, developing and managing other similar work designed, developed and managed by Consultant. Compliance with Applicable Laws and Regulations: Consultant shall abide by all applicable laws, regulations and ordinances of all governmental authorities including local   bodies issuing NOCs and of the administrative subdivisions thereof applicable to  this Contract and the performance by Consultant of the Work in any jurisdiction and by all rules and regulations of those Persons and entities having control or jurisdiction over the Work. Consultant represents that is it fully aware of all of the legal requirements, business practices and rules and regulations which must be followed when performing the Work. Consultant shall furnish to OWNER, promptly upon request, such information concerning Consultant, its Subcontractors and their respective employees,  servants and agents as OWNER may be required to furnish to any applicable governmental agencies or authorities.

  - Permits and Licenses:

    - In Consultant’s Name: Consultant shall obtain and maintain any registrations, licenses (including import licenses), and permits (including immigration, temporary residence, work and exit permits), which are required by Indian laws, or Indian regulations, for the performance of the Work and which are required to be in the name of Consultant, its employees, agents or its Subcontractors.

    - In OWNER’s Name: Consultant shall assist OWNER in obtaining and maintaining (including the preparation and submission to OWNER of all documentation necessary  therefor), any non-Indian registrations, licenses and permits (including import and export licenses for the W ork), which are required to be in the name of OWNER or its employees or agents.

  - Co-operation with, Other Consultant, Contractors and Suppliers:

Consultant shall co-operate with OWNER’s other consultants, contractors and suppliers, provide reasonable access to Consultant’s premises for them and coordinate its activities with the activities of such consultants, contractors and suppliers under OWNER’s direction.

  - Notification of Suits and claims; OWNER’s Right to Defend

    - Consultant to Notify Consultant shall give OWNER immediate written notice of any suit or action filed against Consultant arising out of the performance of the Work, and of any claim against Consultant which if paid could result in a claim by Consultant for indemnification or for which insurance coverage is not in effect or which will be in an amount which exceeds the amount of insurance coverage. Consultant shall promptly furnish to OWNER copies of all papers received by Consultant pertinent to any such suit or action.

    - OWNER’s Right to Defend If requested by OWNER, Consultant shall, do any and all things necessary or appropriate to effect an assignment and subrogation in favour of OWNER of all Consultant’s rights and claims, except against OWNER, arising from or growing out of any suit, action or claim, and shall authorise OWNER or OWNER'’ designated representatives to exercise any such rights to settle or defend any such claims or take charge of any such litigation affecting Consultant. In the event of such a request by OWNER, OWNER shall reimburse Consultant for the costs of such litigation incurred by Consultant, if any, including judgments, settlements, court costs and, if OWNER does not retain its own counsel, reasonable attorney’s fees.

ARTICLE-6

OWNER’S RESPONSIBILITIES

  - OWNER’s Representative: Upon execution of this Contract, OWNER shall designate a representative (“OWNER’s Representative”) who shall be appointed to represent OWNER under this Contract and notice given to and received from OWNER’s Representative shall have the same effect as if given to or received from OWNER. OWNER shall notify Consultant of the designation of the OWNER’s Representative by Delivering to Consultant a letter naming such person or any replacement. Except as expressly stated in this Contract, the OWNER’s Representative shall have no authority to relieve the Consultant of any of its duties, obligations, liabilities or responsibilities under this Contract.

  - Approvals: OWNER shall expeditiously review and pursue documents, drawings, specifications, proposals and requests submitted by Consultant pursuant to this contract. Except as expressly otherwise specified elsewhere in this Contract, OWNER shall respond promptly of receipt of any such submission, in the case of submissions requiring action by governmental agencies or committees, and within 10 days of receipt of any such submission, in the case of submissions requiring action by OWNER only. In case no written advice, comment or instruction is received by Consultant within such periods, or within any periods for review and perusal stated elsewhere in this Contract, each submission for review/comments shall be considered approved; and Consultant shall inform the OWNER of the same in writing.

  - Owners Obligations: All other OWNERS obligations shall be as defined earlier

ARTICLE-7

CONTRACT PRICE, TAXES

  - Contract Price:. In consideration of Consultant agreeing to perform the Work in accordance with this Contract, OWNER shall pay to Consultant the Contract Price according to the terms of payment.

  - Amounts Included in the Contract Price: The Contract Price set forth in this Contract shall be inclusive, without limitation, of all costs, risk and expense, overhead, profit, professional tax, duties prevailing at the time of submission of bids and during execution of the contract except for service tax and cess over it which shall be paid as actuals. Statutory variations to the taxes and duties and imposition of new tax if any shall be paid on actual against submission of documentary proof to this effect. Service tax to be quoted and paid separately. The date of bid submission shall be cut-off date for determining the statutory variations.

  - Taxes and Duties:

    - Taxes & Duties: The contract price set forth in this contract is inclusive of all taxes & Levies like professional tax etc. except service tax &cess. New tax, if any, introduced later shall be on owner’s account from the date of bid submission (or extended date, if any) upto the contract period. Any upward statutory variation (including any new tax) beyond contractual completion date shall be borne by the PMC. However, in case of downward variation, the same shall be passed on to the owner.

    - OWNER’s Right to Withhold: OWNER may withhold or deduct from the payment of any amount otherwise payable to Consultant under this Contract, or pay on Consultant’s behalf, such taxes and other sums, if any, as OWNER may be required to withhold or deduct under the laws of any jurisdiction in India or any political subdivision or taxing authority or agency thereof.

ARTICLE-8

PAYMENT

  - Payment of Contract Price:

The Contract Price shall become payable by OWNER in accordance with the following provisions of this Article.

    - Completion of and Payment for Work Subject to Milestones.

      - Milestones: Details of the Milestones and the percentage of payment to be released on completion of such milestones as annexed herewith under payment terms.

      - Contents of the Certificate: The certificate to be issued by Consultant in respect of each Milestone shall:

a) Identify the Milestone, with reference to the Schedule of Work.

b) Include a statement as to whether the Milestone was properly achieved  in accordance with the Schedule of Work;

c) Specify the Milestone Value claimed.

      - Payment: Consultant shall be entitled to payment for each Milestone properly certified as complete and confirmed by OWNER as achieved in accordance with this Contract as follows:

a) OWNER shall pay to Consultant as per Payment Schedule, in respect of such Milestones as are properly certified as complete by Consultant in respect of each Milestone so certified and confirmed by OWNER, within 30 days of receipt of invoice thereof by OW NER.

b) No additional payment shall be made for any Milestone achieved in advance of the date fixed or period specified thereof in the Schedule of Work.

  - Additional Costs:

    - Additional Costs: Consultant shall not be entitled to any adjustment of the Contract Price to be paid except for any supplemental agreement in writing between OWNER and Consultant providing that any further costs should be paid to the Consultant.

    - Calculation of Cost: Such costs wherever required shall be calculated by reference to the break up of prices and/or unit rates contained in Price Bid or if in OW NER’s opinion there is no applicable price, on the basis of actual cost to Consultant, provided Consultant gives adequate supporting data on actual cost to OWNER’s satisfaction.

  - General Terms of Payment:

    - Accounts: All payments by OWNER to Consultant shall be made through NEFT/RTGS.

    - Effect of Payment: The making of any payment shall in no event constitute the acceptance by OWNER of any Work performed by Consultant pursuant to this Contract.

ARTICLE-9

CHANGES

  - Changes: Consultant agrees to effect such changes in the Work as OWNER may from time to time request. Any request by OWNER for a change shall be delivered to Consultant in writing for Consultant to prepare a preliminary change order. Throughout the performance of the Work, Consultant shall have a continuing obligation to propose to OWNER for OWNER’s consideration all such changes as Consultant considers desirable including, any change which in the Consultant’s opinion will reduce the cost of the Work, / and or Project Facilities or improve the efficiency or value to OWNER, or may otherwise be of benefit to OWNER. Such other changes known to Consultant as may be necessary to incorporate significant new developments in technology which are applicable or appropriate to the Work. Consultant shall submit any such proposal in the form of a preliminary change order.

  - Preliminary Change Orders: Upon receipt of OWNER’s request for a change, Consultant shall prepare a preliminary change order and furnish the same to OWNER within a reasonable period of time following receipt of such request. Each preliminary change order submitted by Consultant to OWNER, shall be in writing and be accompanied by such information and data as will be reasonably required by OWNER to evaluate properly the proposed execution of the work in question, the effect on the Scope of Work, the Schedule of Work, Consultant’s standards of performance, the Engineering Design, the technical soundness of the Work, the other undertakings by Consultant and the warranties contained in this Contract and the effect on the Contract Price, if any. OWNER shall reject or approve each preliminary change order as expeditiously as proper consideration of the nature of the change may reasonably and data required to accompany the preliminary change order involved and for any additional analytical or investigative work requested by OWNER in connection therewith is deemed to be included in the Contract Price.

  - Variations in Price: Except as otherwise provided in this Contract, any increase in costs resulting from any change shall be for the account of OWNER, provided that no cost adjustment shall be granted with respect to a change if, the provision of the additional work or services is necessary in order for Consultant to satisfy its responsibility to make the Work comply with this Contract,  the additional work or services are required because of delays in the Schedule of Work attributable to Consultant, to late deliveries of materials or services or to labour shortages of consultant. The additional work or services are required because of a breach of Consultant’s General Warranties or, the change relates to re-performance of any of the Work because of Consultant’s failure to follow the requirements of this Contract.

  - Non Allowable Changes: The following shall not be considered under any circumstances as changes in the Work, or within or to the Scope of Work or the project management services or the engineering design, nor shall any of the following be taken into account when calculating the cost consequences of changes, nor shall any of the following of themselves be considered the basis for any adjustment: any escalation in the cost of the Work or Materials or labour therefor;  any increase in manpower hourly rates; and /or currency fluctuations in respect of costs included within the Contract Price and / or Re-submission of documents with correctness not less than 98%. In addition, a request by OWNER that Consultant perform services or provide work not specifically included within the Scope of Work will not be considered a request for a change in the Scope of Work, if it is mutually agreed that the services or work requested were intended to be within this Contract or necessary to make the Work comply with this Contract. Consultant shall certify/ settle bills for closing of contract, analyse & provide rate analysis/ verification of new items and abnormal quantity variations, negotiation of rates in respect of upward variations beyond 25 % and abnormal quantity variations for price approved by Owner for all tender packages of the project.

  - CONSULTANT shall also be entitled to price and/or schedule adjustment to reflect the impact of any event not attributable to CONSULTANT, including (a) Change in law or unforeseen site conditions which results any part of CONSULTANT’s services as sins fructuous and needs to be redone. (b) the reason attributable to OWNER. OWNER shall in all above cases extend the Time Schedule and pay reasonable compensation for associated increase in CONSULTANT’s costs provided that such costs are duly documented and mutually agreed.

ARTICLE-10

RIGHT TO INSPECT

  - Inspection and Examination: All management, design, development, Material, Work and workmanship supplied by Consultant or for which Consultant is responsible, shall be subject during normal business hours to inspection, examination and testing by OWNER, OWNER’s Representative, or OWNER’s designated consultants and/or other representatives, at any and all times during management, design and development and at any and all places where such management, design and development are carried on, provided such inspection, examination and testing shall, to the extent possible, be carried out in conjunction with Consultant’s.

  - Rejection and Reperformance: OWNER and its designated consultants and representatives shall have the right to reject any portion of the work which is defective, deficient, not within specifications or otherwise of inferior quality or faulty services and require its re-performance. Rejected and other defective or deficient management or work shall be satisfactorily redone. The costs associated with such re-performance shall be for the account of Consultant and not reimbursable. After completion of the necessary re-performance, the relevant Work shall be subject to further inspection and examination by OW NER and its designated consultants and representatives.

  - Consultant to Furnish Supplies and Services for Inspection: Consultant shall furnish at each location where inspection and examination is carried out all reasonable facilities, assistance, labour and utilities necessary for the safe and convenient inspection of Work that may be required pursuant to this Contract. Consultant shall also furnish OWNER and OWNER’s designated consultants and representatives with access to records of all inspections undertaken by Consultant. Tests shall be conducted in accordance with applicable provisions of this Contract or otherwise as required by OWNER.

  - Consequences of Inspection or Failure to Inspect: The right of inspection and examination by OWNER and by its designated consultants and other representatives provided herein is intended solely for OWNER’s benefit, it being understood that no exercise of or failure to exercise such right shall relieve Consultant of any of its obligations hereunder or prejudice any of OWNER’s rights under this Contract.

ARTICLE-11

ACCEPTANCE PROCEDURE

  - Notice of Acceptance: Consultant shall notify OWNER in writing when Consultant believes that it has completed the entire Scope of Work. Within 30 days after receipt of Consultant’s notice of such completion of the Work, OWNER shall advise Consultant in writing of any portions of the Work which remain to be performed, through a checklist and Consultant shall thereupon complete such portions, as indicated in checklist and again notify OWNER in writing that Consultant confirms that the Work has been completed. OWNER shall issue a certificate of Acceptance of the Work (the “Certificate of Acceptance”), after the Work has been completed and accepted, and dated to reflect the actual date of Acceptance of the Work.

  - Conditions: The issue of the Certificate of Acceptance shall be conditional upon: Legally effective releases, executed by Consultant, and any persons claiming by, through, under or against Consultant who might have an interest in the Work or part adverse to OWNER, of all claims and liens against OWNER arising under or by virtue of this Contract, except such claims and liens, if any, in such stated amounts which Consultant, with the written consent of OWNER, may exclude from operation of such releases; and Consultant’s written declaration, together with such supporting documents as OWNER may reasonably require, that all claims and demands against, and debts incurred by Consultant, in respect of this Contract, have been settled, except claims excluded with the consent of OWNER from the releases referred to in the foregoing clause, and all taxes due and payable by Consultant have been paid or otherwise provided for.

  - Discretion of OWNER: Notwithstanding the foregoing, OWNER, in its sole discretion, may accept the Work at any time and issue a Certificate of Acceptance even if, after corrective measures have been taken by Consultant, the Work as a whole does not satisfy the requirements of this Contract. Such acceptance and such notice shall not relieve Consultant of its obligations under this Contract.

ARTICLE-12

WARRANTIES & GUARANTEES

  - General Warranties: Consultant warrants that:

    - Personnel: All professional personnel of Consultant shall have proper requsite qualifications for the Work assigned to them hereunder.

    - Standard of Care and Work: Consultant shall perform their obligations under this Contract in conformity with the highest standards of care employed by leading engineering firms in the petroleum/Aviation  industry and all Work shall be first class.

    - Management, Design and Development: The management, design and development of the Work shall conform with this Contract and shall be free of defects and deficiencies. The management, design and development shall be such that the Work shall comply with the terms of this Contract and shall meet all design, safety and performance and other criteria as specified herein.

    - Work: The Work shall be fit for the purposes and uses intended and capable of use in the manner contemplated in this Contract.

    - Other Services: All Work performed by Consultant, including, without limitation, inspections performed by Consultant under this Contract, shall be adequate and sufficient for the purposes intended, in conformity with the terms of this Contract and free of defects and deficiencies.

  - Remediation

    - Notice: At any time OW NER may by notice in writing to Consultant, require Consultant to remedy any defect in the Work by re-performance not later than 18 months from date of mechanical completion or 12 months from the date of commissioning, whichever is earlier.

    - Obligation to Remedy Breach: Consultant shall be obligated to effect, at its own expense, in the shortest practicable time, such re-performance of Work as are necessary to remedy such defect. Consultant’s obligation to remedy any defects shall expire 18 months after mechanical completion or 12 months after stablisation / closure of all contracts whichever is earlier. In case of any defect or deficiency in the Work which has not resulted from a failure by Consultant to perform its such defect or deficiency and shall be entitled to reimbursement of the costs associated with the correction thereof . The amount of such costs shall be agreed between the Parties, or in the absence of agreement, decided by the OWNER, and reimbursed.

    - Program for Reperformance: As soon as practicable, and in any event within 5 days after the receipt by Consultant of OWNER’s notice, Consultant will submit for OWNER’s approval a plan for effecting the reperformance required to remedy such defect. If required by OWNER, Consultant shall attend at the Site specified by the OWNER to inspect the defective Work and where appropriate carry out reperformance

    - OWNER’s Recourse: If Consultant does not begin its plan for re-performance within the time mutually agreed, or if Consultant and OWNER fail to reach agreement on such a program within 15 days of the receipt by OW NER of Consultant’s plan submitted, OWNER, after advising Consultant in writing, shall be entitled at its option and at Consultant’s expense to perform or have third parties perform such work as is necessary to remedy or cause to be remedied such defect. Reasonableness of the expenses as aforesaid shall be judged in relation to the expenses that Consultant would have incurred at the time of said re-performance of Work.

    - Other Rights and Remedies: The rights and remedies of OWNER provided are in addition to any other rights and remedies provided at law.

Completion Warranty

    - Project Completion Warranty: Consultant shall commence the work immediately on receiving written instruction to that effect. The work will be progressed in accordance with the agreed schedule. Failing completion of the project as per agreed overall schedule consultant shall pay or allow owner the compensation of 0.5% of the total consultancy charges for every week of delay attributable to consultant subject to a maximum of 5% of the total concluded contract value.

    - Extended stay: Delay due to reasons attributable to the owners shall only be considered for payment on mutually agreed rates post commissioning. Non-performance of Contractors/ Vendors will not be treated as a justification for compensation for extended stay.

    - Performance Guarantee: Consultant undertakes guarantees for performance of the design work entrusted to Consultant who will be obliged to remedy any lack of performance of the guarantees and if for any reason the said guaranteed performance cannot be achieved, a financial liability to the extent of 10 % of consultant’s fees shall be affected.

  - Payments: Any amount required to be paid by Consultant may be deducted by OWNER from any amounts otherwise payable to Consultant.

ARTICLE –13

EFFECT OF APPROVALS, ACCEPTANCE AND PAYMENT

The obligations of Consultant hereunder shall not, except as expressly provided herein, be reduced or affected by any inspection, test, approval or payment, whether preliminary or final, or by the Certificate of Acceptance of the Work, it being agreed that the obligations of Consultant hereunder shall continue until fully satisfied or 18 months from the date of mechanical completion or 12 months from the date of stablisation/ closure of all contracts whichever is earlier.

ARTICLE-14

TITLE

  - Title to Work: Consultant agrees that title to the Work (excluding proprietary items) or any part thereof shall pass to OWNER from Consultant upon commencement of Work from Effective date, or any portion thereof, by Consultant. Consultant shall, however, retain care, custody, and control of the Work and exercise due care thereof. Such transfer of title shall in no way affect OWNER’s rights under any other provision of this Contract.

  - Warranty of Title: Consultant warrants good title to the Work.

  - Protection of Title: For the purpose of protecting OWNER’s interest in all Work with respect to which title has passed to OWNER but which remains in the possession of Consultant or others through Consultant, Consultant shall take or cause to be taken all steps necessary under the laws of the appropriate jurisdictions to protect OWNER’s title and to protect OWNER against claims by other parties with respect thereto.

  - Ownership of Designs and Drawings ; All designs, drawings, specifications, data, computer printouts, programs and files, documents, reports, studies, manuals, programs, analyses and all other items produced by Consultant in the performance of the Work and identified as deliverables, shall become and remain the property of OWNER, and Consultant shall deliver the same (properly sorted and indexed), to OWNER in accordance with the provisions of this Contract and in any event upon termination of this Contract and shall be used only for this project.

ARTICLE-15

PROPRIETARY INFORMATION; DATA; LICENSES AND INVENTIONS

  - Proprietary Information of OWNER. Proprietary Information Defined: “Proprietary Information”, shall mean all information which Consultant, directly or indirectly, acquires from OWNER or its Affiliates or from the performance of the Work, or any other information concerning the technical and business activities and know-how of OWNER or its Affiliates. information obtained by Consultant from a third party who is lawfully in possession of such information and not subject to a contractual or fiduciary relationship to OWNER or any of its affiliates with respect to said information; it being understood that Consultant may use and disclose such information in accordance with the terms under which it was provided by such third party;

    - Consultant’s Procedures: Consultant represents that it has a policy and procedure designed to protect trade secret rights and its own proprietary information including notices to its employees to prevent unauthorised copying, publication and disclosure of such information. Consultant agrees that Proprietary Information shall be subject to such policy and procedure. In addition, Consultant agrees that it shall not disclose any Proprietary Information, nor use Proprietary Information other than on OWNER’s behalf, except as OWNER may otherwise authorise in writing. If disclosure to a third party is so authorised, Consultant shall first enter into a written confidentiality agreement with said party containing the same terms and conditions with respect to use or disclosure of Proprietary Information.

    - Documents: Consultant also agrees to safeguard any documents and information which OWNER may supply to Consultant thereunder. Consultant may make copies of such documents only to the extent necessary for the performance of the Work. On completion of the Work, Consultant agrees to return to OWNER all documents supplied by OWNER and to destroy all copies thereof. Should Consultant, however, desire to retain certain documents and receives OWNER’s written approval therefor, Consultant shall treat said documents as it does Proprietary Information.

    - Confidentiality Agreements with Third Parties: Consultant also agrees to enter into written confidentiality agreements with third parties upon OWNER’s request and to keep in force confidentiality, agreements concerning third parties’ proprietary information, which agreements shall permit Consultant to use such parties’ proprietary information in the Work.

    - Consultant’s Confidential information: It is not OWNER’s desire to be afforded access to Consultant’s confidential information. It is therefore agreed that any information which Consultant supply to OWNER shall not be subject to any obligation of confidence, (notices on drawings, proposals, graphs, tables, specifications and the like to the contrary notwithstanding), and OWNER shall not be liable for any use or disclosure of any of such information unless such information is the subject of an express written confidentiality agreement between OWNER and Consultant. Consultant also agrees that it will not disclose to OW NER any information which is subject to an obligation of confidence by Consultant to any third persons.

Computer Data: Consultant will retain essential/critical backup data, which has been developed for carrying out Engineering Design Package for Consultant designed units for use of the OWNER (other than which is part of deliverable) for 18 months after mechanical completion or 12 months from the date of stablisation/ closure of all contracts, whichever is earlier.

  - Licenses: On or before the date of the Certificate of Acceptance of the Work, Consultant shall deliver or cause to be delivered to OWNER such licenses of all patents and other proprietary rights held by Consultant, any Subcontractor, or any of their respective Affiliates as may be required for OWNER in the optimal use of the Work in the manner intended.

ARTICLE-16

FRUSTRATION

In the event of this Contract being frustrated whether by war or by any other supervening event which may occur independently of the will of the Parties, the sum payable by the OWNER to Consultant shall be the same as would have been payable, if this Contract had been terminated.

ARTICLE-17

FORCE MAJEURE AND EXTENSIONS OF TIME

  - Force Majeure

    - Events of Force Majeure: For purposes of this Contract, “Event of Force majeure” shall mean any circumstance not within the reasonable control of the Party affected and which, despite the exercise of reasonable diligence, such Party is unable to prevent, avoid or remove.

    - Effect of Force Majeure: Should any Event of Force Majeure Prevent or delay the performance by a party of any of its obligations under this Contract (Other than a Payment obligation when, as and if due thereunder) then, provided that notice is given to the other Party, the party which is prevented or delayed in the performance of its obligations, shall be excused from performance or performance in accordance with, the time specified in this Contract, for so long as the relevant event of Force majeure continues, and to the extent that such Party’s performance is prevented, hindered or delayed, such party shall be excused from performance of the obligations prevented, hindered or delayed until the expiration of any extension of time agreed between the Parties or granted to Consultant .

    - Instances of Force Majeure: Events of Force majeure shall include without limitation the following:

a) acts of God;

b) acts of war or the public enemy whether war be declared or not’

c) public disorders, insurrection, revolution, rebellion, sabotage, riots or violent demonstrations;

d) explosions, fires, earthquakes or other natural calamities; and

e) strikes or lockouts or other industrial action by workers or employees, other than Consultant’s or any Subcontractor’s workers or employees.

f) Epidemic

g) Flood

h) Law, order, proclamation, regulations or ordinance of any Government or

subdivision or statutory authority.

    - Notice of Force Majeure; Procedure: If either Party desires to invoke an Event of Force majeure as a cause for delay in the performance of any obligation hereunder, that party shall, not later than 48 hours after the commencement of such Event of Force Majeure, give written notice to the other Party of:

a) the Date of commencement and nature of the Event of Force Majeure; and

b) the Date on which the Event of Force Majeure terminated (if before the Date of notice), alternatively, if the Event of Force Majeure is continuing, its expected duration.

    - Mitigation of Delay: The Party affected by the Event of Force Majeure shall use all reasonable efforts to prevent and reduce to a minimum and mitigate the effect of any delay occasioned by any Event of Force majeure including recourse to alternate acceptable sources of services, and reasonable adjustment of Work activities.

    - Costs During Force Majeure: In the event of an event of Force Majeure, each Party shall bear any costs incurred by it resulting therefrom.

  - Extensions of Time

    - Relevant Events: Consultant may apply to OWNER for an extension of time in respect of any Milestone or portion thereof, if any, if the following events occur (“Relevant Event”), which delay or prevent, or will delay or prevent, Consultant from achieving such Milestone by the time specified in the Schedule of Work:

a) a Change Order under

b) an Event of Force Majeure;

c) a notice of suspension served ;

d) any delay, impediment or prevention by OWNER.

    - Certain Delays not Excused: Consultant shall not be entitled to any extension of time in respect of any delays caused directly or indirectly due to any event which is not expressly provided for as a Relevant Event.

    - Mitigation of Delay: Consultant shall use and continue to use its best endeavours to reschedule work activities to avoid or reduce the effects of any Relevant Event upon achievement of each Milestone.

    - Notice: If Consultant wishes to pursue a claim for an extension of time, Consultant shall, not later than 10 days after the commencement of the Relevant Event in respect of which the extension of time is claimed, give written notice (in addition to any other notice which may be required under this Contract) to OW NER, which:

a) gives full and detailed particulars of the cause of the delay;

b) specifies which of the Relevant Events listed above, Consultant considers to be applicable;

c) gives the date on which the Relevant Event relied upon commenced, and, if the Relevant Event has ceased, the date on which it ceased, or, if the Relevant Event is continuing, the expected duration; and

d) gives full and detailed particulars of:

i. The effect of any delay to date and of any further delay which may reasonably be expected upon the Schedule of Work; and

ii. The measures which Consultant has adopted to date and / or proposes to adopt or continue to adopt in order to minimise the effects of any delay to date and of any future delay.

    - Procedure: Upon receipt of a notice served, OWNER and Consultant shall endeavour to agree the period of extension of time in respect of the relevant Milestone(s), if any, to which Consultant is entitled and any necessary consequential adjustments to the Schedule of Work. Any such agreement shall be recorded in writing signed by OWNER and by Consultant.

ARTICLE –18

SUSPENSIONS

  - Suspension: OWNER may at any time, and from time to time, and for any reason, by written notice to Consultant, suspend further performance of the Work or any portion thereof. Any notice of suspension shall specify the date of suspension and the estimated duration of the suspension. Upon the date specified in any such notice of suspension, Consultant shall promptly suspend further performance of the Work and during the period of such suspension shall properly care for and protect the Work including all design work in progress. OWNER may, at any time, terminate the suspension by written notice to Consultant specifying the effective date of termination, and Consultant shall use its best efforts to resume performance of its obligations pursuant to this Contract immediately upon receipt of such notice. If Consultant’s performance of the Work has been delayed as a result of such a suspension, the Consultant shall be entitled to an extension of time.

  - Costs During Suspension: OWNER shall pay to Consultant additional costs resulting solely from a suspension of the Work provided suspension period exceeds 90 days in continuation, on mutually agreed basis. Each such suspension period will be reckoned as the period starting with the date of notice of suspension and ending with the date of notice of its termination; for Suspension of portion of Work, the additional cost will be agreed between Consultant and OWNER on mutually agreed basis, depending on impact of such Suspension; provided however, that OWNER shall not be liable for any payment to the extent that such suspension is attributable to Consultant’s failure to perform under this Contract.

ARTICLE-19

TERMINATION

  - OWNER’s Right to Terminate: OWNER may terminate this Contract as follows:

    - Convenience: OWNER may terminate this Contract for its convenience at any time and without cause. In such event, OWNER shall give Consultant not less than 30 days written notice of its decision to terminate this Contract.

    - Force Majeure: If an Event of Force Majeure continues for more than 3 (three) months after the notice of the Event of Force Majeure is properly given, and if the Event of Force Majeure has rendered impossible the performance of this Contract, then OWNER may terminate this Contract by giving Consultant at least 30 days prior written notice of termination.

    - Default: If Consultant shall assign or transfer this Contract or any right or interest herein, except as permitted; or if the interest of Consultant shall devolve upon any person or corporation otherwise than as herein permitted; or if Consultant shall fail without cause to make timely payment for labour, services or Materials, or disregard laws or ordinances or lawful requirements of any competent governmental authority, or instructions of OWNER; or if, Consultant shall fail, neglect, refuse of be unable at any time during the course of the Work to perform the Work at a rate deemed sufficiently by OWNER to give reasonable assurance that Consultant will complete the Work in accordance with the Scope of Work; or if Consultant otherwise commits a material breach of its obligations under this Contract; and, in the case of any of the foregoing events, if capable of remedy, Consultant fails to remedy such breach within 30 days after receiving written notice thereof from OWNER, OWNER may terminate this Contract forthwith, by giving Consultant written notice of such immediate termination.

    - Bankruptcy, Liquidation: If Consultant shall become voluntarily or involuntarily the subject of proceedings under any bankruptcy or insolvency law, or other law or procedure for the relief of financially distressed debtors, or is unable, or admits its inability, to pay its debts as they mature, or takes or suffers any action for its liquidation or dissolution, or has a receiver or liquidator appointed for all or any part of its assets, OWNER may terminate this Contract by giving Consultant written notice of immediate termination. In the event that such notice is not given for any reason, Consultant shall remain fully responsible for its obligations set forth in this Contract at the times required.

  - Consultants Right to Terminate

    - Default: If OWNER Commits a material breach of its obligations under this Contract and fails to remedy such breach within 60 days after receiving written notice thereof from Consultant, Consultant may terminate this Contract by giving OWNER written Notice of immediate termination.

    - Force Majeure: If an Event of Force Majeure continues for more than 6 months after the notice of the Event of Force Majeure is properly given and if the Event of Force Majeure has rendered impossible the completion of the Work, in accordance with the Schedule of Work and the terms of this Contract, then Consultant may terminate this Contract by giving OWNER at least 30 days prior written notice of termination.

    - Suspension: If performance of the Work shall have been suspended by OWNER for a period of at least 6 consecutive months, and if by the end of such 6 months period OWNER shall not have issued a notice of termination of such suspension, Consultant may give OWNER 30 days prior written notice of Consultant’s intention to terminate this Contract. If OWNER terminates the suspension by written notice during such period of 30 days, Consultant shall resume performance of its obligations under this Contract. If the OW NER does not issue such notice, Consultant’s notice of termination shall take effect on the expiration of the period of 30 days.

    - Bankruptcy, Liquidation: In case of bankruptcy or liquidation of OW NER, Consultant shall have right to terminate the Contract.

  - Effect of Termination: If this Contract is terminated , the following provisions shall apply:

    - Calculation of Work Value: Immediately upon notice of termination of this Contract by either Party, the Parties shall consult with one another in order to agree on the percentage of Work completed up to the date of termination. It is understood that resolution of disagreement, if any, in arriving at completed work value will be a matter of arbitration.

    - Payment Obligations on Termination: Without prejudice to any rights and remedies which OW NER or Consultant may otherwise have, if this Contract is terminated, OWNER shall, pay to Consultant:

a) an amount equal to (C x P/100) – PVW where C is the Contract Price, P is the Work Value and PVW is that part of the Contract Price actually paid to Consultant.

b) all costs which are additional and incurred to the Date of termination, and remaining unpaid; and

c) except in the case of a termination, reasonable proper and unavoidable costs incurred as a direct result of termination, including costs of any cancellation charges that Consultant is obligated to pay as a result of such termination, provided Consultant submits adequate proof/supporting data on such costs to OWNER’s satisfaction. OWNER shall pay to Consultant such amounts after receipt of an invoice therefore, shall apply to such payment. Consultant shall make every effort to minimise the changes referred to this sub-clause (c). All amounts payable to Consultant shall be mutually agreed upon by OW NER and Consultant.

    - Termination for Default or Bankruptcy: In the case of termination by OWNER for default or bankruptcy in the circumstances, amounts due to OWNER and Consultant on the date of termination shall be settled based on mutual agreement.

    - Accrued Liabilities: Accrued liabilities of Consultant, and any liabilities (actual or potential) of Consultant for acts and omissions with respect to Work partially or fully completed at the time of termination shall not be affected by any such termination.

    - Option to Take Over Work: In the event of a termination of this Contract, OWNER shall have the right to delivery and possession of the partially completed Work and to finish the W ork itself or with the assistance of third parties.

  - Effect of Termination Generally: If this Contract is terminated for any reason, Consultant shall take immediate steps to bring its services to a close in a prompt and orderly manner and shall make every effort to keep expenditures for that purpose to a minimum. Consultant shall preserve and protect all Work and all property of OWNER subject to Consultant’s supervision, shall deliver or relinquish such Work and such other property to or as directed by OW NER and shall assign to OWNER such of Consultant’s subcontracts, purchase orders and other commitments as OWNER may request.

ARTICLE-20

MANAGEMENT, KEY PERSONNEL AND PROJECT DIRECTOR

  - General: Consultant shall provide, maintain and be responsible for all management during the performance of the Work. Consultant’s procedures for managing, designing and developing the Work shall generally be those of Consultant, which are subject to review and/or approval by OW NER. The project activity shall be carried out activity -wise to accomplish the project schedule. OWNER shall have the right, but not the obligation, to be represented at the Consultant’s offices to liaise closely with Consultant’s management during the performance of the Work. This representation may include appropriate management, technical, administrative and clerical personnel to review and/or approve Work performed by Consultant.

  - Key Personnel:

    - Consultant shall provide dedicated team as per Organogram proposed by them and accepted by the Owner for executing this Project. The details of key personnel to be submitted along-with their bids. Proposed Organogram should reflect Project Manager as Project Incharge with RCM reporting to him functionally.

    - OWNER may notify Consultant at anytime that individuals filling positions described in the staff organisation plan are Key Personnel. Consultant shall procure (so far as in within its power), that Key Personnel shall be employed on or in relation to the Work full time until the issue of the Certificate of Acceptance of the Work. In the event that it becomes necessary to replace any or all Key Personnel, Consultant shall provide alternative personnel acceptable to OWNER with such skills, experience and knowledge that will fully fulfill the role of the individuals replaced in achieving completion of the Work in accordance with this Contract. Such replacement shall take place within 10 days of non-availability of the Key Personnel being replaced. Consultant agrees that such replacement will be avoided to the extent possible except as may be required by OWNER and that any such replacement will be carried out without delaying any Project Schedule. All key personnel shall be fluent in the English language.

  - Project Co-ordinator: Consultant shall appoint, subject to OWNER’s prior, written approval, a fully qualified, experienced and competent Project Co-coordinator who shall have complete and entire responsibility for executing all Work to OWNER’s satisfaction. The Project Co-ordinator shall be the formal focal point for all OWNER related communications and management related matters and shall be fully authorised to bind Consultant for all purposes under this Contract.

  - OWNER/Consultant Interface: Consultant shall co-ordinate and interface with OWNER’s Representative during the performance of the Work.

  - Reporting: Consultant shall, in accordance with the requirements contained in Scope of Work, periodically furnish OWNER with reports, tabulations and charts containing all necessary information that will permit OWNER to review and analyse the status of Work.

  - Meetings: Consultant shall, at OWNER’s option attend meetings at OWNER’s premises or other designated locations. Consultant shall be responsible for recording all minutes of meetings. The minutes of meetings shall be circulated by Consultant for OWNER’s approval and OWNER shall notify its concurrence thereto or any amendments thereto, Consultant representatives for attending all such meetings is deemed to be included in the Contract Price.

  - Site Supervision: The Consultant shall observe all rules and regulations relating to the Site and the Work as are notified to it by the Site supervisor, OWNER or OWNER’s Representative.

ARTICLE-21

INSURANCE AND INDEMNIFICATION

  - Consultant shall take out and maintain valid, for its personnel and property, such insurance policies as may be required by applicable Indian Laws.

  - Consultant and its Sub-contractors shall hold harmless and indemnify OWNER including OWNER’s agents, servants or employees against any claims, loss or liability for personal injury or death, or damage to Consultant property, and arising out of or connected with the W ork performed under this Contract.

  - OWNER shall take out and maintain relevant insurance cover for all imported and indigenous equipment and materials to cover marine risk, transportation and storage-cum-erection. All costs incurred in this behalf shall be borne directly by OWNER.

ARTICLE-22

PATENT INDEMNIFICATION

  - Indemnity: Consultant shall indemnify OWNER against all loss, cost, damage and expense arising from any claim asserted against OWNER, that the Work or part thereof, or any methods, designs or things furnished or specified by Consultant under this Contract, or any use thereof in the reasonable contemplation of the Parties at the time furnished, or any methods, processes or acts employed by Consultant in connection with the performance of its obligations hereunder, constitutes an infringement of any intellectual property right, patent, trade secret, proprietary information, know-how, copyright (statutory or non-statutory), unpatented invention or any unauthorised use of the work of others.

  - Defence of Claims: Consultant shall at its own expense defend any suit or proceeding based on any claim asserted against OWNER. OWNER shall give Consultant such assistance as Consultant may reasonably require in the defence of such suit, and shall have the right to be represented therein by counsel of its own choosing at its own expense. Neither OWNER nor Consultant shall settle or compromise any such suit or action without the written consent of the other if the settlement or compromise obligates the other to make any payments or part with any property or assume any other obligations or other rights or be subject to any injunction by reason of such settlement or compromise.

  - Persons included within Indemnity: the term OWNER shall include OWNER, its Affiliates and their respective officers, directors, employees, servants, consultants and agents, or any of them as the context may require.

  - OWNER shall also have obligations as specified above for the information, data, input, etc., supplied by OWNER or by others on behalf of OW NER.

ARTICLE-23

GOVERNING LAW AND DISPUTES

  - The Contract shall be governed by laws of the Republic of India.

  - General: Any dispute or difference of any kind whatsoever between OWNER and Consultant arising under, out of or in connection with this Contract (including without limitation any question regarding its existence, validity or termination), or the execution of the work including without limitation any dispute as to any decision, opinion, OWNER’s Representative whether during the execution of the Work or after completion or delivery thereof and whether before or after the termination, abandonment or breach of this Contract, shall be amicably settled .

  - Notice: Each Party shall notify the other in writing when it considers a dispute or difference has arisen and which it wishes to refer to the other party or difference has arisen and which it wished to refer to the other Party for amicable settlement, and to arbitration, in the event that amicable settlement is not reached. Such notice shall contain sufficient information as to the dispute or difference to enable the other Party to be fully informed as to the nature of the dispute, the amount of any monetary claim and the length of any extension of time claimed.

  - Amicable Settlement: Where notice of dispute or difference has been given, the parties shall attempts to settle such dispute amicably before commencement of arbitration, provided that unless the Parties agree otherwise, such dispute may be referred to arbitration subject to after the sixtieth day after the day on which notice of dispute or difference was given, even if no attempt at amicable settlement has been made.

  - Arbitration:

    - Any ‘dispute or difference of any nature whatsoever, any claim, cross-claim, counterclaim or set off of the Owner against the Consultant or regarding any right, liability, act, omission or account of any of the parties hereto arising out of or in relation to this agreement shall be refereed to the Sole Arbitration of the  nominated Director  of the Owner or of some Officer of the Owner who may be nominated by the nominated Director . The consultant will not be entitled to raise any objection to any such arbitrator on the ground that the arbitrator is an officer of the Owner or that he has dealt with the matters to which the contract relates or that in the course of his duties as an Officer of the Owner, he had expressed view on all or any other matters in dispute or difference. In the event of the arbitrator to whom the matter is originally referred being transferred or vacating his office or being unable to act for any reason, the nominated Director  as aforesaid at the time of such transfer, vacation of office or inability to act may in the discretion of the nominated Director designate another person to act as arbitrator in accordance with the terms of the agreement to the end and intent that the original Arbitrator shall be entitled to continue the arbitration proceedings notwithstanding his transfer or vacation of office as an officer of the Owner if the nominated Director does not designate another person to act as arbitrator on such transfer, vacation of office or inability of original arbitrator. Such person shall be entitled to proceed with the reference from the point at which it was left by his predecessor. It is also a term of this contract that no person other than the nominated Director  of the Owner or a person nominated by such nominated Director as aforesaid shall act as arbitrator hereunder. The award of the arbitrator so appointed shall be final, conclusive and binding on all parties to the agreement subject to the provisions of the Arbitration & Conciliation Act,1996 or any statutory modification or reenactment thereof and the rules made there under for the time being in force shall apply to the arbitration proceedings under this clause.

    - The arbitrator shall have power to order and direct either of the parties to abide by, observe and perform all such directions as the arbitrator may think fit having regard to the matters in difference i.e. dispute, before him. The arbitrator shall have all summary powers and may take such evidence oral and/or documentary, as the arbitrator in his absolute discretion thinks fit and shall be entitled to exercise all powers under the Indian Arbitration & Conciliation Act 1996 including admission of any affidavit as evidence concerning the matter in difference i.e. dispute before him.

    - The parties against whom the arbitration proceedings have been initiated, that is to say, the Respondents in the proceeding, shall be entitled to prefer a crossclaim, counter claim or set off before the Arbitrator in respect of any matter in issue arising out of or in relation to the Agreement without seeking a formal reference of arbitration to the nominated Director/officer  for such counter-claim, or set off and the Arbitrator shall be entitled to consider and deal with the same as if the matters arising therefore has been referred to him originally and deemed to form part of the reference made by the nominated Director/officer.

    - The arbitrator shall be at liberty to appoint, if necessary any accountant or engineering or other technical person to assist him, and to act by the opinion so taken.

    - The arbitrator shall have power to make one or more awards whether interim or otherwise in respect of the dispute and difference and in particular will be entitled to make separate awards in respect of claims of cross claims of the parties.

    - The arbitrator shall be entitled to direct any one of parties to pay the costs to the other party in such manner and to such extent as the arbitrator may in his discretion determine and shall also be entitled to require one or both the parties to deposit funds in such proportion to meet the arbitrators expenses whenever called upon to do so.

    - The parties hereby agree that the courts in the city of Delhi alone shall have jurisdiction to entertain any application or other proceedings in respect of anything arising under this agreement and any award or awards made by the Sole Arbitration hereunder shall be filed (if so required) in the concerned courts in the city of delhi only.

ARTICLE-24

MISCELLANEOUS

  - Independent Contractor: Consultant is an independent contractor under this Contract, and shall have complete charge of all personnel performing any Work under this Contract. Consultant shall perform all Work in accordance with its own methods and shall be fully responsible for the Work performed in accordance with the terms of this Contract.

  - Assignment: This Contract shall be binding upon and shall inure to the benefit of the Parties and their respective successors-in-interest and duly permitted assigns.

    - Assignment by OWNER: OWNER may, written intimation to the Consultant, assign the benefit of this Contract, or any part thereof and any interest therein or thereunder, to an Affiliate.

    - Assignment by Consultant: Consultant may not assign the benefit of this Contract or any interest therein or thereunder to any third party, without written consent of OWNER. Any assignment by Consultant without prior written consent of OWNER shall by null and void and of no force or effect whatsoever.

  - Entire Contract; Modifications; This Contract constitutes the entire agreement between OWNER and Consultant concerning the subject matter hereof. All previous documents, undertakings and agreements, whether oral or written, between the Parties concerning the subject matter hereof are hereby cancelled and shall not affect or modify any of the terms or obligations set forth in this Contract, except as the same may be made part of this Contract in accordance with its terms. No modifications to this Contract shall be made except by written agreement between the Parties, except as otherwise expressly provided in this Contract.

  - Resolution of Inconsistencies: In the event of any inconsistency between any of the Articles or Sections of this Contract, and any Exhibit to this Contract, the Articles or Sections of this Contract shall prevail subject thereto, the provisions of this Contract shall be mutually explanatory. If any inconsistency in this Contract shall become apparent, it shall be resolved by OWNER in writing in consultation with Consultant and in accordance with the foregoing order of priority. Consultant shall immediately notify OWNER of any inconsistency which Consultant discovers.

  - Waiver: The failure of either Party to insist upon strict adherence to any term of this Contract on any occasion shall not be considered a waiver of any right thereafter to insist upon strict adherence to that term or any other term of this Contract. Any waiver must be made in writing.

  - Language: The official text of this Contract shall be in the English language. Except as otherwise specifically provided to the contrary, all documents, advisement’s, notices, waivers and all other communications, written or otherwise, between OWNER and Consultant in Connection with this Contract shall be in the English language, and Consultant shall ensure that all agreements and communications between Consultant and others shall be in the English language.

  - Metric System: Except as otherwise specifically provided to the contrary, all documents, references to weights and measures to be made hereunder; shall be expressed in the metric system, including, without limitation, drawings, plans, specifications, design, surveys, estimates, reports and all other documents and Work originated by Consultant.

  - Notices: All notices required to be given under this Contract by OWNER to Consultant shall be in writing and delivered at the address as indicated from time to time.

  - Effectiveness of Agreement: This Contract shall become effective on the date of LOI (the ‘EFFECTIVE DATE’) and the Parties shall become bound by all conditions applicable to their conduct pursuant to this contract from the Effective Date.

ARTICLE-25

LIMITATIONS OF LIABILITY

  - Overall Limit: Consultant’s maximum overall liability limit for all guarantees, warranties, liquidated damages and other liabilities of whatsoever nature, whether expressed or implied, shall be limited to 10% of the contract value effectively received by CONSULTANT.

  - Consequential Damages: Neither Party shall be liable to the other Party for any indirect or consequential damages in connection with or arising out of this Contract including, but not limited to, loss of use, revenue or profit.

ARTICLE-26

CONSULTANT shall not issue tender to any of their associate companies.

ARTICLE-27

At all stages of the design/engineering/construction phases of the project, consultant should build in suitable provisions to enable future expansion, change in configuration of project.

8.0.	SPECIAL CONDITIONS OF CONTRACT

  - All the papers related to submission of Solvency certificate, Income Tax clearance certificate, Credentials of the bidder, Experience of the bidder, Copies of work order for the works carried out during the last five years, Documents to confirm the present status of these works, Works in hand, Availability of manpower under their command, should be enclosed alongwith the bid.

  - Bidder shall keep offer valid for a minimum of six months from the bid due date of this tender.

  - Incomplete bids, conditional bids or bids received late or bid not conforming to the terms and conditions prescribed in NIT are liable to be rejected.

  - The OWNER reserves the right to accept any bid in whole or part and reject any bid without assigning any reason. The OWNER is not bound to accept the lowest or any other bid and reserves the right to accept one or more bids in part. The decision of OWNER in this regard shall be final.

  - Highest standards of safety shall be maintained at site and all safety precautions and regulations should be strictly adhered to. Compliance to OISD guidelines/ certificate may be obtained.

  - Electrical works: All electrical works to be carried out through licensed Electrician/ supervisor only.

  - Taxes & duties: The bidder must quote the rates including all prevailing taxes, statutory levies, sales tax and works contract tax, professional tax, etc. Service tax to be mentioned separately. OWNER shall not entertain any request for payment of any taxes/levies separately. The cut-off date for any statutory variation will be bid due date/ extended bid due date, as the case may be.

  - OWNER reserves the right to revise the specifications, drawings and designs at any stage of work. Such deviations shall be adjusted at the prevailing market rate or mutually agreed rate, rate supported by valid and detailed rate analysis build up, man-hourly/ man-monthly rate available in the contract if the rates of such deviation items are not available in the contract.

  - When the party signing the agreement is not the sole proprietor, the necessary Power of attorney authorising the person who is acting on behalf of the proprietor should be produced before execution of the Agreement.

J.	Price Bid

J.1	The bidder shall quote in the enclosed price bid formats, lumpsum price for providing consultancy services for OWNER’s proposed project as detailed in this tender.

J.2	The price and man-hour, man-month rates quoted by the bidder shall be valid for a period of six months from the due date of the e-tender and shall continue to remain valid thereafter till pendency of agreement / closing of contract.

J.3	Further the price and man-hour, man-month rates quoted by the successful bidder shall remain firm during the tenure of the contract.

J.4	The bidder shall quote man-hour, man-month rates for various categories of manpower.

K.	Basis of Lump sum Prices & Other Rates

The fixed lump sum prices and other rates set forth herein shall be inclusive of all costs, risks and expenses, Service Tax, professional tax, taxes including withholding taxes, overhead, profit and / or total fee related to the satisfactory performance and completion of the work. Lump sum price quoted shall also include overheads / all expenses viz. setting up Camp offices, Site offices at various spreads etc.. Consultant to indicate the present rate of service tax and the amount thereof in their price bid, separately. The lumpsum prices for Scope of work more explicitly described in Chapter “Project Management Consultant’s Scope Of Work/Services” of “NIT” and other rates shall include any and all costs related to management, supervision, design, engineering, surveys, attendance at all meetings with OWNER (whether at OWNER’s premises;  OWNER’s nominated location or Consultant’s premises; any other location applicable during contract phase of the project), inspection, testing and quality assurance / quality control of the work, as more particularly described in the scope of work, or elsewhere in the contract. Said lump sum prices and other rates shall include, but not be limited to the costs of all labour, supervision, management, (including but not be limited to, wages, benefits, payroll, taxes, travel, accommodation expenses and other costs thereto as are paid to employees), all equipment, communications equipment, communication charges (including those incurred by OWNER while in consultant’s offices), all administrative costs of consultant’s operation, all reproduction and graphic costs of whatever kind, postage and courier expenses, all insurance requirements and coverage, and all other costs or expenses of any kind which directly or indirectly relate to accomplishing the work and complying in full with the provisions of the contract, and which are not otherwise set forth or referred to in the Contract as reimbursable expense.

Specifically, the lump sum quote of the consultant should include all the expenses in setting up of camp offices, site offices with necessary infrastructure facilities transportation and other incidental changes for inspection and also for statutory approvals. Prices for inspection assignment in foreign countries (Foreign travel expenses all inclusive per person for total number of persons earmarked for the same ) and , travel in India including accommodation, will be paid separately shall not included in quoted Lump sum rates at mutually agreed rates.

L.	The OWNER reserves the right to reject any or all tenders without assigning any reasons whatsoever.

M.	Running Account payments to the Consultant shall be linked to the milestones devised for total completion of the project. The break up of lump sum prices into milestones is only to facilitate payment to the bidder at desired intervals and that milestones break up is based on the entire scope of work entrusted to the consultant. Individual prices do not hold good on standalone basis.

N.	Payment for each of the milestones shall be released only after completion of all activities contained in that particular milestone. The amounts payable to the consultant on completion of each milestone shall be equivalent to the percentage indicated against the milestones in the Payment Schedule.

O.	Bidders are required to submit the price bid strictly in accordance with the price bid format attached. The price bid format blanking off the price figures should also be submitted along with Unpriced Bid.

9.0.	PRICE BID FORMAT

A.	Lumpsum charges for providing Consultancy services. The consultant charges  for  inspection and travel, if any  would be paid separately on submission of actual bills as described under 1.5. AMOUNT Lumpsum charge for providing consultancy services as detailed in this tender under Following heads :

1a.  Office work Rs.

1 b. Site work Rs.

Total 1 (a+b) Rs.

Total in words (a+b) ---------------Service

tax value ( ____%) __________

Education cess ( ____%) __________

Total value

__________

B.	Break up estimated Man – hours / Man – month indicated in items 1 a and 1 b shall be provided in following format:

2a. Man-hours for office work

2b. Man-month for site work

The above estimated man-hours for office and man-months for site work shall be used for evaluation purpose only.

C.	Man months as per the agreed organogram shall be provided by the consultant and if man-months actually spent on the project are found lesser then the contractual amount shall be suitably reduced after mutual agreement as per rates provided in this clause no. 3 below .

3a) Man-Hours Rate for Office work Grade / Designation No. of Estimated Man hours Rate Amount

Persons (Rs.) (Rs.)

1. ……… ……. ……… ……… ………

2. ……… ……. ……… ……… ……….

3. ……… ……. ……… ……… ……….

4. ……… ……. ……… ……… ……….

Total (3a) ……… ………. ………..

3b) Man-month Rate for site work

Grade / Designation

No. of Estimated Manmonth Rate Amount

Persons (Rs.) (Rs.)

1. ……… ……. ……… ……… ……..

2. ……… ……. ……… ……… ………

3. ……… ……. ……… ……… ………

4. ……… ……. ……… ……… ………

Total (3b) ……… ……… …………

D.	For additional work / services to be performed from office/ site: Consultant’s man-hour, man-month rate shall be as follows :

D.1	Applicable during tenure of contract period

    - Man-Hour, Man-Month Rate for Office work Grade / Designation Man-Hour rate Man-Month rate (Rs.) (Rs.)

    - Man-Hour, Man-Month Rate for site work Grade / Designation Man-Hour rate Man-Month rate (Rs.) (Rs.)

    - Man-day rate for works outside India Grade / Designation rate (Rs.)

D.2	Applicable beyond contract period for a period of 6 months

- 4.2.1 Man-Hour, Man-Month Rate for Office work Grade / Designation Man-Hour rate Man Month rate (Rs.) (Rs.)

- 4.2.2 Man-Hour, Man-Month Rate for site work Grade / Designation Man-Hour rate Man-Month rate (Rs.) (Rs.)

- 4.2.3 Man-day rate for works outside India Grade / Designation rate (Rs.)

NOTE: The above man-hour, man-month rates shall be all inclusive of all overheads, charges etc. and no claim whatsoever shall be entertained over and above quoted rates except for service tax &cess.

10.0.	PAYMENT SCHEDULE

Payment shall be made to successful Bidder against milestones completion / progress. Typical milestone guidelines are given below. Bidders are advised to adhere to the following milestones. The bidder shall relate these milestones to detailed network of the project.

Milestones for Payment to CONSULTANT

  - Office Work -Annexure-I

  - Site work -Annexure-II

ANNEXURE – I

DAFFPL PROJECT BILLING BREAK UP SCHEDULE AGAINST MILESTONE ACHIEVED FOR OFFICE WORK / HO SERVICES

MILESTONE % WTGE

- finalization & submission of Process Package including data sheets & P&IDs and approval from OWNER - 10

- Completion of Detailed Engineering / Drawing / tendering / evaluation / recommendation for award - 20

- On finalisation of MRs / Drgs. / RFQ / receipt / evaluation / recommendation for award – 10

- On preparation & submission of approved for construction drawings (AFC) drawings - 10

- On receipt of materials at site with relevant operational/ maintenance manuals - 10

- On submission of AS-BUILT drawings for all facilities - 5

- On successful commissioning of project - 25

- On closing of contracts/ Orders - 10

Detailed break-up of weightage against each head shall be discussed & mutually agreed with selected PMC.

ANNEXURE – II

BILLING BREAK UP SCHEDULE AGAINST MILESTONE ACHIEVED FOR SITE WORK

MILESTONE % W TGE

- Mobilization of RCM and Spread In charges & Required manpower - 10

- Progressive payment on monthly basis based on construction progress - 75

- Within 30 days of commissioning or within 90 days from the date of successful Mechanical completion, whichever is earlier - 5

- Final documentation - 5

- After completion of SAT’s and post commissioning stabilization (5 months period from date of commissioning) - 5

Detailed break-up of weightage against each head shall be discussed & mutually agreed with selected PMC.

11.0.	ANNEXURES

ANNEXURE-A

EXCEPTION AND DEVIATIONS STATEMENT

Bidder may stipulate exceptions and deviations to tender document, if considered unavoidable as per the following format:

Sl. No.    Page No of Bid Document    Clause No.    Subject Deviations

All exceptions / deviations taken by bidder to the stipulations of the tender document shall be brought out in the techno-commercial bid (and not in the tender document or Price Bid ) as per this format. Any exceptions/ deviations brought out elsewhere in the bid shall not be construed as valid.

SIGNATURE OF BIDDER:

NAME OF BIDDER :

SEAL :

ANNEXURE-B

PROFORMA OF BANK GUARANTEE

(EARNEST MONEY DEPOSIT)

(On Non-Judicial Stamp paper for appropriate value)

BANK GUARANTEE NO. :

BANK GUARANTEE AMOUNT :

CLAIM :

(till 120 days from date of work order )

TENDER NO. /DATE :

JOB DESCRIPTION/

LOCATION :

Tender Security No. [*]

Name and Address of the Beneficiary:  Delhi Aviation Fuel Facility (P) Ltd., New Udaan Bhawan, New Delhi – 110037, India

We [name and address of the issuing bank] have been informed that [Name of the Interested party] (hereinafter called the “Interested Party”) is submitting a proposal  for the Award of the Works in response to a tender by Delhi Aviation Fuel Facility (P.) Ltd. (“DAFFPL” or ‘Beneficiary”) for [Insert description of work] (“Works”). The conditions of the tender, which are set out in a documents entitled Request for Proposal dated [Please insert] require its offer to be supported by a Tender Security.

At the request of the Interested Party, we hereby irrevocably undertake to pay you without demur, the Beneficiary, any sum or sums not exceeding Rs. _________ [Please insert].

Upon receipt by us of your demand in writing and your written statement (in the  demand) stating that:

- The Interested Party has, without written consent of DAFFPL, withdrawn its offer after the latest time specified for its submission and before the expiry of its period of validity; or

- The Interested Party has refused to accept the correction of errors in nits offer in accordance with the instructions to Interested parties contained in the TENDER; or

- DAFFPL entered in to the contract with the Interested party but the Interested party has failed to deliver the COMPOSITE BANK GUARANTEE (SECURITY DEPOSIT & PERFORMANCE) in compliance with the Contract conditions; or

- The Interested Party has failed to enter into the Contract within 30 (Thirty) days of being required to do so by the Tender Officer.

Any demand for payment must contain your signature(s). The demand must be received by us at this office on or before the expiry of the earliest of the following dates, when this security guarantee shall expire and shall be returned to us:

- Date of issue of letter communicating to the Interested Party that it has not qualified for the contract or the Proposal submitted by the Interested Party is unsuccessful or the TENDER is withdrawn and/or cancelled by the Beneficiary; or

- 7 (seven) days after the date of delivery of an acceptable performance bond complying with the Contract conditions and execution of the Contract after the award of the works to the Interested Party; or

- 120 (One hundred twenty) days from the last date of submission of Proposal in accordance with the TENDER.

Date:

Signature:

Designation:

Name of the Branch

ANNEXURE-C

PROFORMA OF COMPOSITE BANK GUARANTEE (SECURITY DEPOSIT & PERFORMANCE)

(On Non-Judicial paper of Rs. 100/-value)

To,

DAFFPL

Dear Sirs,

M/s ………………………………………………….have taken tender for the work  …………………………for DAFFPL,.

The tender Conditions of Contract provide that the Contractor shall pay a sum of Rs. ………….. (Rupees …………….. ) as security deposit & performance guarantee in the form therein mentioned. The form of payment of security deposit & performance guarantee includes guarantee executed by Scheduled Bank at New Delhi, undertaking full responsibility to indemnify DAFFPL, in case of default. The said party ………………………… have approached us at and their request and in consideration of the premises we ……………….. having our office at ………………. have agreed to give such guarantees as hereinafter mentioned.

- We --------------------------------------------------hereby undertake and agree with you that if default shall be made by M/s. -----------------------------------------------in performing any of the terms and conditions of the tender or in payment of any money payable todaffpl. We shall on demand pay to you, without demur, protest or requiring you to seek recourse to M/s __________________________, in such matter as to you may direct the said amount of Rupees ----------------------------------------------------------only or such portion thereof not exceeding the said sum as you may from time to time require.

- You will have the full liberty without reference to us and without effecting this guarantee, postpones for any time or from time to time the exercise of any of the powers and rights conferred on you under the contract with the said ------------------------------------and to enforce or to forbear from endorsing any powers of rights or by reason of time being given to the said ------------------------------------------which under law relating to the sureties would but for provision have the effect of releasing us.

- Your right to recover the said sum of Rs. ---------------------------------------------------(Rupees ------------------------------------------------------------------------) from us in manner aforesaid will not be affected or suspended by reason of the fact that any dispute or disputes have been raised by the said M/s. -----------------------------------------------and/or that any dispute or disputes are pending before any officer, tribunal or court.

- The guarantee herein contained shall not be determined or affected by the liquidation or winding up dissolution or change of constitution or insolvency of the said -------------------------------------------but shall in all respect and for all purposes be binding operative units payment of all money due to you in respect of such liabilities is paid.

- Our liability under this guarantee is restricted to Rupees -------------------------------our guarantee shall remain in force until -------------------------------------unless a suit or action to enforce a claim under Guarantee is filed against us within six months from --------------------------------------------------(which is date of expiry of guarantee) all our rights under the  said guarantee shall be forfeited and we shall be relieved and discharged from all liabilities thereunder.

- NOT WITHSTANDING anything hereinbefore contained our liability under this Bank Guarantee is restricted to Rupees ------------------------( Rupees -----------------------------------).This Bank Guarantee shall be valid upto -----------------------and we are liable to pay the guaranteed amount or any part thereof under this Bank Guarantee only and only if you serve upon us a written claim or demand on or before.

- This guarantee is to be returned to us within fifteen ( 15 ) days from the date it ceases to be in force. If the guarantee is not returned to us within the date of aforementioned it shall be automatically cancelled.

- We have power to issue this guarantee in your favour under Memorandum and Articles of Association and the undersigned has full power to do under the Power of Attorney dated ---------------granted to him by the Bank.

Yours faithfully

-----------------------------------Bank

by its Constituted Attorney

Signature of a person duly

Authorised to sign on behalf of the bank

Annexure- D

Form of Letter of Undertaking

[On the letterhead of the Interested Party]

Letter of Undertaking

Date:

Delhi Aviation Fuel Facility (Private) Limited

Terminal 3 Project Offices, Opposite Terminal-3,

IGI Airport, New Delhi – 110 037, India

Tel.	+ 91-11-[4608 4240],

Re:

The undersigned Interested Party acknowledges that the TENDER issued is confidential and personal to the undersigned Interested Party and hereby undertakes and agrees as follows:

1.	“Confidential Information” means the TENDER and everything contained therein, all documentation, data, particulars of the Works and technical or commercial information made by (or on behalf of) Delhi Aviation Fuel  (Private) Limited or obtained directly or indirectly from Delhi Aviation Fuel  (Private) Limited or its representatives by the undersigned Interested Party or which is generated by the undersigned Interested Party or any information or data that the undersigned Interested Party receives or has access to, as a result of the TENDER, as being confidential information of Delhi Aviation Fuel (Private) Limited, provided that such term does not include information that (a) was publicly known or otherwise known to undersigned Interested Party prior to the time of such disclosure, (b) subsequently becomes publicly known through no act or omission by undersigned Interested Party or any person acting on its behalf.

2.	The undersigned Interested Party shall maintain the confidentiality of Confidential Information in accordance with procedures adopted by the undersigned Interested Party in good faith to protect confidential information of third parties delivered to it, provided that the undersigned Interested Party may deliver or disclose Confidential Information to its authorized representatives who agree to hold confidential the Confidential Information substantially in accordance with the terms of this Undertaking,

3.	The undersigned Interested Party shall not at any time whatsoever:

(i)	Disclose, in whole or in part, any Confidential Information received directly or indirectly from the Delhi Aviation Fuel (P) Limited to any third party.

(ii)	Reproduce, publish, transmit, translate, modify, compile or otherwise transfer the Confidential Information.

4.	In case the Proposal of the undersigned Interested Party is not accepted and immediately upon the acceptance of the Proposal of any of the other Interested Party, the undersigned Interested Party, shall:

(i)	Return all Confidential Information including without limitation, all originals, copies, reproductions and summaries of Confidential Information; and

(ii)	Destroy all copies of Confidential Information in its possession, power or control, which are present on magnetic media, optical disk or other storage device, in a manner that ensures that the Confidential Information is rendered unrecoverable.

5.	The undersigned Interested Party shall certify to Delhi Aviation Fuel t (Private) Limited that it has returned or destroyed such Confidential Information to the Delhi Aviation Fuel  (Private) Limited within two (2) days of such a request being made by Delhi Aviation Fuel  (Private) Limited.

Name of Interested Party’s	 of Authorized Representative

Signature